## Sheet1
Question # | Question Text | Correct Answer (Letter) | Answer Text | Book Title | Chapter | Page Range | Explanation / Summary
Water transmission and distribution
| Water velocities through pipe should be limited to 5 ft /sec in order to a. minimize friction loss. b. reduce the number of pressure reducing stations. c. minimize destruction of piping appurtenances. d. reduce the amount of corrosion inhibitors applied to piping. | a | Minimize friction loss | Water Transmission and Distribution | 2 | 14–15 | Velocities should normally be limited to about 5 ft/sec in order to minimize friction loss.
| What pipe joint is commonly used for ductile iron piping? a. Expansion joint b. Push-on joint c. Bell and spigot with rubber o-ring d. Rubber gasket joint | b | Push-on joint | Water Transmission and Distribution | 2 | 28–30 | Push-on joints are cost-effective, easy to install, and provide watertight seals.
| The C-value is a measure of a pipe’s wall a. smoothness. b. smoothness giving even flow. c. smoothness that retards turbulent flow. d. roughness that retards flow due to friction. | b | Smoothness giving even flow | Water Transmission and Distribution | 2 | 20 | The C-value measures pipe smoothness; higher values = smoother pipe = less friction.
| The fire insurance underwriters recommend that no main should have a diameter less than a. 3 inches. b. 4 inches. c. 6 inches. d. 8 inches. | c | 6 inches | Water Transmission and Distribution | 2 | 14 | Fire underwriters recommend no main be less than 6 inches to provide adequate flow.
| The highest degree of protection for the exterior of a coated steel pipe is a. cathodic protection. b. bituminous materials. c. plastic coatings. d. polyethylene tapes. | a | Cathodic protection | Water Transmission and Distribution | 2 | 33 | Cathodic protection helps prevent soil-based corrosion when combined with coatings.
| A plat is a. a map. b. a corrosion point on a pipe. c. organelle found in some protozoans. d. a highly corrosive soil type. | a | Map | Water Transmission and Distribution | Glossary
| Which type of valve will prevent the collapse of a pipe? a. Pressure-relief valve b. Needle valve c. Pinch valve d. Vacuum relief valve | d | Vacuume Relief Valve | Water Transmission and Distribution | 2 |  | (The design for proper vacuum relief should be checked by methods detailed in AWWA Manual M11
| The highest degree of protection for the exterior of a coated steel pipe is a. cathodic protection. b. bituminous materials. c. plastic coatings. d. polyethylene tapes. a. cathodic protection. b. bituminous materials. c. plastic coatings. d. polyethylene tapes. a. cathodic protection. b. bituminous materials. c. plastic coatings. d. polyethylene tapes. | a | Cathodic protection | Water Transmission and Distribution | 2 | 33 | For the highest degree of protection, a coated pipeline is commonly also provided with cathodic protection.
| At which time of day is the age of the water stored in the distribution system the highest? a. Early morning b. Late morning c. Early afternoon d. Late evening | a | early morning | Water Transmission and Distribution | 5 | pg 115 | Review of composite usage patterns suggests that typically, water age due to storage in the water distribution system is highest in the early morning hours and lowest in the late evening
| The C-value is a measure of a pipe’s wall a. smoothness. b. smoothness giving even flow. c. smoothness that retards turbulent flow. d. roughness that retards flow due to friction. | d | Roughness that retards flow due to friction | Water Transmission and Distribution | 2 | 20 | The C-value measures pipe smoothness; higher values = smoother pipe = less friction.
| Which one of the following is a type of joint for ductile iron piping? a. Expansion joint b. Push-on joint c. Bell and spigot with rubber o-ring d. Rubber gasket joint | b | Push-on joint | Water Transmission and Distribution | 2 | 28–30 | Push-on joints are cost-effective, easy to install, and provide watertight seals.
| The correct protective methods for backflow-prevention devices in order of decreasing effectiveness are a. air gap, VB, RPZ, and DCVA. b. air gap, VB, DCVA, and RPZ. c. air gap, RPZ, VB, and DCVA. d. air gap, RPZ, DCVA, and VB. | d | air gap, RPZ, DCVA, and VB. | Water Transmission and Distribution | 11 |  | The preventive measure chosen depends on the degree of hazard involved, how accessible the premises are, and the type of water distribution system within the cross-connection location backflow-prevention devices, in order of decreasing effectiveness, are 1.air gaps 2. reduced pressure zone backflow preventers 3.double check valve assemblies 4. vacuum breakers (atmospheric and pressure) 5. barometric loops.
| After a water storage tank has been chlorinated, which bacteriological test must prove negative before the tank is put back into service? a. Gram negative test b. HPC test c. Coliform test d. Chloramine test | c | Coliform test | Water Transmission and Distribution | 3 | 68 | After the chlorination procedure is completed, and before the tank is placed in service, water from the full tank must be tested for bacteriological safety (coliform test).
| It is standard practice to install fire hydrants on mains that are at a minimum ____________ or larger. a. 6 inches b. 8 inches c. 10 inches d. 12 inches | a | 6 inches | Water Transmission and Distribution | 7 | 163 | Standard practice is to install hydrants only on mains 6 in. (150 mm) or larger. Larger mains are often necessary to ensure that the residual pressure during fire flow remains greater than 20 psi (140 kPa).
| A corporation stop is used for a a. service line. b. pump discharge line. c. tank inlet. d. tank outlet. | a | service line. | Water Transmission and Distribution | 6 | 138 | The valves used to connect water services to water mains are usually referred to as corporation stop.
| When PVC pipe is stacked loose, it should not be stacked more than how high? a. 2.0 feet b. 3.0 feet c. 5.0 feet d. 7.5 feet | b | 3 Feet | Water Transmission and Distribution | 12 | 307 | Leave PVC pipe in shipping units until needed. Do not stack pipe more than three bundles high. If it is loose, do not stack more than 3 ft (0.9 m) high. Protect the pipe from sunlight with a canvas tarpaulin or other opaque material. Do not use clear plastic sheets, and allow air to circulate beneath the cover
| Which is the most common cause for pipe joint failure (leaking) in newly laid pipe? a. The use of a cracked gasket b. Not pushing the spigot end the full distance into the bell c. Not having the joint completely clean d. An incorrect trench bedding angle | c | Not having the joint completely clean | Water Transmission and Distribution | 12 | 325 | The most common cause of joint failure is not having the joint completely clean.
| Compression fittings used with copper or plastic tubing seal by means of a a. beveled sleeve. b. compression ring. c. compressed beveled gasket. d. compressed o-rings located at either end of the fitting’s beveled neck. | c | compressed beveled gasket. | Water Transmission and Distribution | 15 | 416 | Flare fittings are available for connecting lengths of copper tubing and adapting to iron pipe thread. The same fittings can be used for plastic pipe of the same dimensions. Compression fittings can be used with either copper or plastic tubing or iron or lead pipe. These fittings seal by means of a compressed beveled gasket. Compression fittings also have a gripping mechanism that positively secures the pipe or tubing. When they are used for PE or PB plastic tubing, it is also recommended that an insert stiffener be placed inside the tube to strengthen the joint. Where stray currents are a problem, dielectric couplings should be used to prevent corrosion.
| The breaking of a buried pipe when it is unevenly supported is called a. stress breakage. b. shear breakage. c. beam breakage. d. flexural breakage. | c | beam breakage. | Water Transmission and Distribution | 2 |  | Beam breakage, which resembles a shear break, may occur when a pipe is unevenly supported along its length
| Thrust from a water surge almost always acts __________ to the inside surface that it pushes against. a. vertically b. horizontally c. perpendicular d. vertically and horizontally | c | perpendicular | Water Transmission and Distribution | 12 | 336 | Thrust almost always acts perpendicular to the inside surface it pushes against.
| Which thrust control is easy to use, especially in locations where existing utilities or structures are numerous? a. Restraining fittings b. Tie rods c. Thrust anchors d. Thrust blocks | a | Restraining fittings | Water Transmission and Distribution | 12 | 338 | Restraining fittings, which make use of clamps and anchor screws, are coming into more general use for restraining joints because they are so easy to use.
| The backfill material for a pipe installation should contain enough __________ to allow for thorough compaction. a. moisture b. sand c. gravel d. mixed sizes | a | moisture | Water Transmission and Distribution | 13 | 343 | appropriate authority. Granular material or selected soil should be used for the first layer of backfill. If soil is used, it must be either carefully selected excavated soil or imported material. Native soil can be used if it does not contain large rocks, roots, organic material. Backfill material should contain enough moisture to permit thorough compaction. The backfill should have no large rocks, roots, construction debris, or frozen material in it.
| Which type of valve is used to isolate a pump on the suction side? a. Butterfly valve b. Globe valve c. Gate valve d. Ball valv | c | Gate Valve | Water Transmission and Distribution | 4 | 75 | Gate valves are used in the suction piping in order to isolate the pump, with the valve stem installed horizontally to avoid air pockets.
| Water hammer can be described as a. particle waves. b. acoustic waves. c. rogue waves. d. longitudinal waves. | b | acoustic waves. | Water Transmission and Distribution | 5 | 127 | Hydraulic transient flow occurs when flow changes suddenly from one steady-state flow to another steady-state flow. Transient flow is the intermediate stage flow during the transition. This hydraulic transient is also referred to as water hammer. By definition, water hammer is a pressure (acoustic) wave phenomenon created by relatively sudden changes in liquid velocity
| When fully opened, which valve will have the highest head loss? a. Gate valve b. Plug valve c. Globe valve d. Ball valve | c | Globe valve | Water Transmission and Distribution | 6 | 149 | Although they seat very tightly, globe valves produce high head loss when fully open. They are not suited for distribution mains where head loss is critical.
| Which type of pressure sensor uses a wire fastened to a diaphragm? a. Bellows sensor b. Strain gauge c. Helical sensor d. Diaphragm element | b | Strain gauge | Water Transmission and Distribution | 9 | 211 | Strain gauges The diaphragm strain gauge sensor is the type used most widely in modern instrumentation. As shown in Figure 9-1A, it consists of a section of wire fastened to a diaphragm. As the variable being measured (such as pressure) changes, the diaphragm moves, changing the length of the wire, thus increasing or decreasing its resistance. This changing resistance can be measured and transmitted by electrical circuits. Similar electronic sensors include the variable-capacitance pressure cell, variable-reluctance pressure cell, and vibrating wire
| Why is it so important to monitor the speed of a variable-speed pump? a. To prevent excessive temperatures from developing b. To prevent vibration from developing c. To prevent speed oscillation from occurring d. To prevent cavitation from occurring | d | To prevent cavitation from occurring | Water Transmission and Distribution | 4 | 93 | Monitoring the pump speed of variable-speed pumps is important because these pumps may experience cavitation (the creation of vapor bubbles) at low speeds.
| The first oil change on a new pump should be done a. after the first two weeks of operation. b. after one month of operation. c. after three months of operation. d. after six months of operation. | b | after one month of operation. | Water Transmission and Distribution | 4 | 104 | The bearing housing of oil-lubricated bearings should be kept filled with a good grade of filtered mineral oil. The oil should be changed after the first month of operation of a new pump.
| All sensors that respond to liquid pressure will perform poorly if ________ enter(s) the sensor. a. air b. corrosive chemicals from water treatment processes c. corrosive chemicals from piping d. iron bacteria | a | Air | Water Transmission and Distribution | 9 | 237 | Every sensor that in any way responds to liquid pressure will perform poorly if air enters the sensor. Air or gas may enter into the sensing element when released from the fluid line. A vent should be provided on the mechanism and used on a regular basis to allow any accumulated air to escape
| Which is the approximate angle of repose for average soils when using the sloping method for the prevention of cave-ins? (Note: horizontal to vertical distance, respectively) a. 0.5 : 1.0 b. 1.0 : 1.0 c. 1.5 : 1.0 d. 2.0 : 1.0 | b | 1.0 : 1.0 | Water Transmission and Distribution | 12 | 316 | Figure 12-9
1 | At which time of day is the age of the water stored in the distribution system the lowest? a. Early morning b. Late morning c. Early afternoon d. Late evening | d | late evening | Water Transmission and Distribution | 5 |  | Review of composite usage patterns suggests that typically, water age due to storage in thewater distribution system is highest in the early morning hours and lowest in the late evening
| Which type of maps should not overlap each other? a. Index maps b. Comprehensive maps c. Construction maps d. Sectional maps | d | Sectional maps | Water Transmission and Distribution | 16 | 438 | Sectional maps should not overlap each other. Instead they should butt up against one another to avoid confusion. Each section should be indexed (individually numbered) and should show matching points for adjacent sections. Indexing sectional maps is not difficult, and the comprehensive map should be used as a base map for indexing.
| Which one of the following is a type of joint for ductile iron piping? a. Welded joint b. Expansion joint c. Flexible ball joint d. Bell and spigot with rubber o-ring | c | Flexible ball joint | Water Transmission and Distribution | 2 | 27 | Flexible Ball Joint
| The fire insurance underwriters recommend that no main should have a diameter less than a. 3 inches. b. 4 inches. c. 6 inches. d. 8 inches. | c | 6 inches. | Water Transmission and Distribution | 2 |  | Fire insurance underwriters recommend that no main in the distribution system be less than 6 in
| Water velocities through pipe should be limited to 5 ft /sec in order to a. minimize friction loss. b. reduce the number of pressure reducing stations. c. minimize destruction of piping appurtenances. d. reduce the amount of corrosion inhibitors applied to piping. | a | minimize friction loss. | Water Transmission and Distribution | 2 |  | Velocities should normally be limited to about 5 ft/sec (1.5 m/sec) in order to minimize friction loss as water flows through the pipe
| Which of the following is a type of joint for polyvinyl chloride piping? a. Bell and spigot type b. Thermal butt-fusion c. Expansion joint d. Restrained joint | a | Bell and spigot type | Water Transmission and Distribution | 2 | 27 | Bell and spigot type
| Which of the following is a type of joint for high-density polyethylene piping? a. Bell and spigot type b. Thermal butt-fusion c. Push-on joint d. Restrained joint | b | Thermal butt-fusion | Water Transmission and Distribution | 2 | 27 | Thermal butt-fusion
| Which of the following is a type of joint for ductile iron piping? a. Welded joint b. Restrained joint c. Expansion joint d. Rubber gasket joint | b | Restrained joint | Water Transmission and Distribution | 2 | 27 | Restrained joint
10 | Which of the following is a type of joint for ductile iron piping? a. Welded joint b. Bell and spigot joint c. Expansion joint d. Flanged joint | d | Flanged joint | Water Transmission and Distribution | 2 | 27 | Flanged joint
| Water mains should primarily be sized based on a. earthquake size potential. b. peak domestic and commercial demands. c. peak commercial and industrial demands. d. adequate fire flow at an appropriate pressure. | d | adequate fire flow at an appropriate pressure. | Water Transmission and Distribution | 2 |  | Mains are sized to provide adequate fire flow. Because the domestic use of a few houses requires much less water than fire flow
| The most desirable residential pressure ranges from a. 20 to 35 psi. b. 35 to 50 psi. c. 50 to 75 psi. d. 75 to 90 psi. | c | 50 to 75 psi. | Water Transmission and Distribution | 2 | 14 | Residential water pressure of between 50 and 75 psi (345 and 517 kPa) is usually considered most desirable
| Which is pipe strength expressed in? a. Hydrostatic potential b. Psi and durability c. Tensile and flexural strength d. Baud units | c | Tensile and flexural strength | Water Transmission and Distribution | 2 | 19 | Pipe strength is expressed in terms of tensile strength and flexural strength.
| The resistance of a material to longitudinal pulling forces before it breaks is called a. flexural strength. b. shear strength. c. ductile strength. d. tensile strength. | d | tensile strength. | Water Transmission and Distribution | 2 |  | Tensile strength is a measure of the resistance a material has to longitudinal, or lengthwise, pull before that material fails.
| Most water systems use hydrants with two nozzles with diameters of ______ and one nozzle with a diameter of ________. a. 2.0 inches; 3.0 inches b. 2.0 inches; 4.0 inches c. 2.5 inches; 3.5 inches d. 2.5 inches; 4.5 inches | d | 2.5 inches; 4.5 inches | Water Transmission and Distribution | 7 | 170 | The smaller-diameter outlet nozzles are for connecting to fire hoses. The larger nozzle, called a pumper outlet or steamer outlet, is used for connecting to a pumper suction hose
| Which type of pipe is durable and strong, has high flexural strength and good corrosion resistance, and is easily tapped? a. High-density polyethylene b. Steel c. Ductile iron d. Reinforced concrete | c | Ductile iron | Water Transmission and Distribution | 3 | 26 TABLE 2-1 | Durable, strong, high flexural strength, good corrosion resistance, lighter weight than cast iron, greater carrying capacity for same external diameter, easily tapped
| Which of the following is a type of joint for concrete piping? a. Expansion joint b. Push-on joint c. Bell and spigot type d. Flanged joint | c | Bell and spigot type | Water Transmission and Distribution | 2 | 27 | Bell and spigot type
| Comprehensive maps of medium to large systems generally have scales ranging from a. 250 to 500 feet to 1 inch. b. 500 to 1,000 feet to 1 inch. c. 1,000 to 1,500 feet to 1 inch. d. 1,500 to 2,000 feet to 1 inch. | b | 500 to 1,000 feet to 1 inch. | Water Transmission and Distribution | 16 | 436 | Comprehensive maps or sometimes referred to as a wall map) provides a clear picture of the entire distribution system. Because the primary purpose of the map is to provide an overall picture, the map’s scale should be as large as possible. Typical comprehensive maps have scales ranging between 500 and 1,000 ft to 1 in.
| Sectional maps generally have scales ranging from a. 50 to 100 feet to 1 inch. b. 100 to 200 feet to 1 inch. c. 200 to 250 feet to 1 inch. d. 250 to 400 feet to 1 inch. | a | 50 to 100 feet to 1 inch. | Water Transmission and Distribution | 16 | 436 | A sectional map or plat ( reference Figure 16-5 on page 436) provides a detailed picture of a section of the distribution system used for day-to-day operations. Use it to find locations and valving of existing mains, the locations of fire hydrants, and the locations of active service lines. Therefore, several maps are required to cover the entire system. Typical scales range from 50 to 100 ft to 1 in.
| Which of the following is a type of joint for steel piping? a. Flexible ball joint b. Restrained joint c. Expansion joint d. Push-on joint | c | Expansion joint | Water Transmission and Distribution | 2 | 27 | Expansion joint
| Which of the following is a type of joint for steel piping? a. Flexible ball joint b. Rubber gasket joint c. Restrained joint d. Galvanized steel ring | b | Rubber gasket joint | Water Transmission and Distribution | 2 | 27 | Rubber gasket joint
| The pressure during fire flow conditions should not drop below a. 15 psi. b. 20 psi. c. 25 psi. d. 30 psi. | b | 20 psi. | Water Transmission and Distribution | 2 | 14 | The required pressure during fire flow conditions should not drop below 20 psi (140 kPa).
| During a fire flow event, the residual pressure in a large main should be greater than a. 15 psi. b. 20 psi. c. 25 psi. d. 35 psi. | b | 20 psi | Water Transmission and Distribution | 7 | 163 | Standard practice is to install hydrants only on mains 6 in. (150 mm) or larger. Larger mains are often necessary to ensure that the residual pressure during fire flow remains greater than 20 psi (140 kPa).
| Which type of distribution system configuration has smaller mains that generally terminate as dead-ends? a. Grid system b. Dendritic system c. Arterial-loop system d. Tree system | d | Tree system | Water Transmission and Distribution | 2 | 10 | tree system brings water into an area with a transmission main, which then branches off into smaller mains. The smaller mains generally end up as dead ends.
| Which is applied to electrodes placed in the water of a water storage tank? a. AC current b. DC current c. An electrolytic inhibitor around the seals where the wires enter the electrodes d. Nothing | b | DC current | Water Transmission and Distribution | 3 | 63 | If electrodes are placed in the water and a direct current is impressed on them, the electrodes will corrode (or “be sacrificed”) instead of the tank
| The frequent starting of distribution system pumps probably indicates a. pump is overheating. b. inadequate supply to pump or check valve leaking back. c. inadequate distribution storage. d. pump is in need of maintenance. | c | inadequate distribution storage. | Water Transmission and Distribution | 3 | 46 | If there is no storage at all, the utility must continually match the changing demand by selecting pumps of varying sizes. Frequent cycling of pumps (i.e., turning them on and off frequently)
| Which needs to be determined first when designing a pump station? a. Discharge requirements b. Head requirements c. Power requirements d. Capacity requirements | b | Head requirements | Water Transmission and Distribution | 4 | 77 | The design of a pump station requires the determination of the head requirements, which can be expressed as a system head curve, including the static or pressure difference and the system friction (head loss).
| Which type of pipe joint consists of two machined surfaces? a. Restrained joint b. Push-on joint c. Flanged joint d. Mechanical joint | c | Flanged joint | Water Transmission and Distribution | 2 | 29 | Flanged joints consist of two machined surfaces that are tightly bolted together with a gasket between them. They are primarily used in exposed locations where rigidity, self-restraint, and tightness are required, such as inside treatment plants and pump stations.
| Which type of pipe joint requires a movable follower ring? a. Flanged joint b. Grooved joint c. Restrained joint d. Mechanical joint | d | Mechanical joint | Water Transmission and Distribution | 2 | 29 | A mechanical joint is made by bolting a movable follower ring on the spigot to a flange on the bell. The follower ring compresses a rubber gasket to form the seal.
38 | What is the height limit to which siphoned water can be lifted at sea level? a. 22.4 feet b. 32.0 feet c. 33.9 feet d. 34.0 feet | c | 33.9 FEET | Water Transmission and Distribution | 11 | 279 | Backflow due to backsiphonage Because backsiphonage is actually caused by atmospheric pressure, the height to which siphoned water can be lifted is limited to 33.9 ft (10.3 m) at sea level. This is the point at which the downward pressure caused by the weight of a column of water equals the pressure of the atmosphere forcing it upward
| How many times higher than the normal operating pressure should the pressure rating of distribution system piping be? a. 1.0 to 2.0 times b. 2.5 to 4.0 times c. 4.0 to 5.0 times d. 5.0 to 7.0 times | b | 2.5 to 4.0 times | Water Transmission and Distribution | 2 | 19 | Distribution system pipe should have a pressure rating of 2.5 to 4 times the normal operating pressure.
| Which type of pipe has been banned in the water industry? a. Ductile iron b. Steel c. Asbestos cement d. High-density polyethylene | c | Asbestos cement | Water Transmission and Distribution | 2 | 23 | Asbestos–cement pipe (ACP) was available in the United States starting around 1930 but is no longer used The US Environmental Protection Agency (USEPA) banned most uses of asbestos in 1989
| Which of the following types of pipe comes in diameters as large as 168 inches (14 feet)? a. Cast-iron pipe b. Reinforced concrete c. Ductile iron d. Prestressed concrete | b | Reinforced concrete | Water Transmission and Distribution | 2 | 26 | Reinforced concrete
45 | Which type of pipe has the highest normal maximum working pressure? a. Reinforced concrete b. Ductile iron c. Polyvinyl chloride d. High-density polyethylene | b | Ductile iron | Water Transmission and Distribution | 2 | 26 | Ductile Iron
| Which type of pipe has the lowest normal maximum working pressure? a. Reinforced concrete b. Ductile iron c. Polyvinyl chloride d. High-density polyethylene | c | Polyvinyl chloride | Water Transmission and Distribution | 2 | 26 | Polyvinyl chloride
| Ductile iron piping using flexible ball joints is most appropriate for a. low-pressure applications. b. high-pressure applications. c. river crossings or rugged terrain. d. all locations. | c | river crossings or rugged terrain. | Water Transmission and Distribution | 2 | 27 | river crossings or rugged terrain.
| Ductile iron piping using push-on or mechanical joints is most appropriate a. for low-pressure applications. b. for high-pressure applications. c. for river crossings or rugged terrain. d. where flexibility is required. | d | where flexibility is required | Water Transmission and Distribution | 2 | 27 | where flexibility is required
| Polyvinyl chloride piping using solvent weld joints is most appropriate a. only for small lines. b. for high pressure applications. c. where flexibility is required. d. where valves or fittings are to be attached. | a | only for small lines. | Water Transmission and Distribution | 2 | 27 | only for small lines.
| Concrete piping using bell and spigot type joints is appropriate a. for all locations. b. where expansion or contraction will occur. c. under low-pressure applications. d. under high-pressure applications. | a | for all locations | Water Transmission and Distribution | 2 | 27 | for all locations
51 | Which type of pipe joint is available in both bolted and boltless flexible pipe joint designs? a. Ball and socket joint b. Push-on joint c. Grooved joint d. Shouldered joint | a | Ball and socket joint | Water Transmission and Distribution | 2 | 29 | Both bolted and boltless flexible pipe joints designed on the ball-and socket principles are available.
| Which type of pipe joint permits flexible pipe alignment, is inexpensive to manufacture, and is easy to assemble? a. Mechanical joint b. Push-on joint c. Grooved joint d. Ball and socket joint | b | Push-on joint | Water Transmission and Distribution | 2 | 30 | Push-on joints are both less expensive to manufacture and quicker to assemble than mechanical joints because there are no bolts to install.
| Which type of pipe joint has machined ends? a. Restrained joint b. Flanged joint c. Mechanical joint d. Shouldered joint | d | Shouldered joint | Water Transmission and Distribution | 2 | 31 | The ends of the pipe are machine-grooved to accept the housing
| New polyvinyl chloride pipe has a C-value of about a. 125. b. 125 to 128. c. 135. d. 150+. | d | 150+. | Water Transmission and Distribution | 2 | 37 | Advantages of PVC pipe include a C value of at least 150
| Which of the following water storage facilities is most likely to contain non-potable water? a. Standpipe b. Buried storage tanks c. Emergency storage tanks d. Elevated tanks using a riser; one way in and one way out | c | Emergency storage tanks | Water Transmission and Distribution | 3 | 49 | Because emergency storage water is not constantly being turned over, it stagnates, loses all residual chlorine, and can become contaminated. It is not usable as a potable water source unless it is further treated.
| Which type of valve is used on hydraulic lines connected to valve actuators? a. Pinch valve b. Needle valve c. Pressure-relief valve d. Vacuum-relief valve | b | Needle valve | Water Transmission and Distribution | 6 | 150 | A common water utility practice is to install needle valves on the hydraulic lines to valve actuators. The needle valves then allow the opening and closing speeds of the actuator to be adjusted.
| Which type of valve would be particularly useful for throttling the flow of corrosive liquids? a. Diaphragm valve b. Butterfly valve c. Gate valve d. Pinch valve | d | Pinch valve | Water Transmission and Distribution | 6 | 150 | This type of valve is available only in relatively small sizes, but it is particularly useful for throttling the flow of liquids that are corrosive or might clog other types of valves.
| Water meter pits are usually used in a. areas where flooding will most likely occur. b. areas where flooding is very rare. c. cold climates. d. hot climates. | c | cold climates. | Water Transmission and Distribution | 15 | 412 | Where meter pits are used in cold climates, the meter can still be raised to near the top of the pit to facilitate reading; meters will not freeze in these locations.
61 | Regarding fire flow, mains smaller than 6 inches should only be used a. in residential areas. b. in low-value districts. c. in rural areas. d. to complete a grid. | d | to complete a grid. | Water Transmission and Distribution | 2 | 14 | Mains smaller than 6 in. (150 mm) should be used only when they complete a desirable grid.
| Which type of pipe requires special external protection in high-chloride soils? a. Reinforced concrete b. Ductile iron c. Steel d. High-density polyethylene | a | Reinforced concrete | Water Transmission and Distribution | 2 | 26 | Reinforced concrete
| Which type of pipe would most likely collapse or become distorted under a partial vacuum? a. Asbestos-cement b. Steel c. Cast iron d. Plastic | b | Steel | Water Transmission and Distribution | 2 | 33 | Steel
| Casing pipe used to house a large water main under a railroad crossing should have a diameter that is ___________ larger than the outside diameter of the water main bells. a. Half the Diameter b. 6 to 10 inches c. 2 to 8 inches d. Same Diameter | c | 2 to 8 inches | Water Transmission and Distribution | 12 | 335 | The most common method of installing a water main under these conditions is to install a casing pipe and then place the water main inside it. When a casing pipe is used for highway or railroad crossings, the project must meet applicable federal, state, and local regulations, as well as any requirements of the highway department or railroad company The casing pipe diameter should be 2–8 in. (50–200 mm) larger than the outside diameter of the water main bells.
| Data manipulations using the basic elements of an automatic mapping (MS)/Facility mapping (FM)/Geographic Information Systems (GIS) would include a. collection and storage. b. collection and management. c. modeling and analysis. d. retrieval, display, and storage. | c | modeling and analysis | Water Transmission and Distribution | 16 | 446 | Basic elements of an AM/FM/GIS The basic elements of an AM/FM/GIS to handle geographic information include data entry (collection, management, and storage), data manipulation (modeling and analysis), and data output (retrieval, management, display, and storage).
| Which data category for water utility data sets includes the following map layers: Control information, planimetric features, and hydrology features? a. Land records data b. Natural resources data c. Watershed resources data d. Base data | d | Base data | Water Transmission and Distribution | 16 | 450 TABLE 16-3 | Base data: Control information Planimetric features Hydrology features
| Which is the proper detention time for disinfecting a water storage tank that is filled with already chlorinated water such that the free chlorine residual is 10 mg/L after the proper detention time is completed? a. 4 hours b. 6 hours c. 8 hours d. 24 hours | b | 6 hours | Water Transmission and Distribution | 3 | 67 | In the first method, the volume of the entire tank is chlorinated, so that the water will have a free chlorine residual of at least 10 mg/L after the proper detention time. The detention time is 6 hours.
| Which is the proper detention time for disinfecting a water storage tank with water that is mixed with hypochlorite already in the tank such that the free chlorine is 10 mg/L after proper detention time is complete? a. 6 hours b. 8 hours c. 12 hours d. 24 hours | d | 24 hours | Water Transmission and Distribution | 3 | 67-68 | if the disinfecting water is chlorinated before entering the tank, and 24 hours if the water is mixed with hypochlorite in the tank.
| Usually the best disinfectant to use in large-diameter pipes or very long pipelines is a. calcium hypochlorite. b. sodium hypochlorite. c. chlorine gas. d. chloramines. | c | chlorine gas. | Water Transmission and Distribution | 13 | 353 | Large-diameter pipes or very long pipelines are usually best disinfected with chlorine gas, but special equipment, procedures, and safety precautions are required
| Which is the available chlorine concentration used for disinfecting a water storage tank using a method that involves spraying or painting of all the interior tank surfaces? a. 50 mg/L b. 100 mg/L c. 200 mg/L d. 250 mg/L | c | 200 mg/L | Water Transmission and Distribution | 3 | 68 | Disinfection After cleaning and/or painting are complete, water storage tanks must be disinfected before being placed in service. Either (1) liquid sodium hypochlorite solution or (2) calcium hypochlorite granules or tablets may be used. Alternate methods of chlorination are listed in AWWA Standard C652, Disinfection of Water-Storage Facilities (most recent edition). The second method involves spraying or painting all interior tank surfaces with a solution of 200 mg/L available chlorine. This procedure requires special precautions and should be done only by trained, experienced, and properly equipped personnel
| When following a two-step process for disinfecting a water storage tank, the initial dosage of 50 mg/L available chlorine should be held in the partially filled tank for a. at least 6 hours. b. at least 10 hours. c. at least 24 hours. d. at least 3 days. | a | at least 6 hours. | Water Transmission and Distribution | 3 |  | Step 1. 6 percent of the tank volume is filled with a solution of 50 mg/L available chlorine for at least 6 hours. Step 2 Then the tank is completely filled and the solution held for 24 hours.
| Why are altitude valves used on water storage tanks? a. To allow water to pass in and out of the tank as pressure fluctuates b. To stop the flow of water into the tank when it is full c. To allow overflow water to flow out of the tank d. To shut the flow of water to the tank off for maintenance and inspection | b | To stop the flow of water into the tank when it is full | Water Transmission and Distribution | 3 | 50 | Occasionally, system pressure could become so high that the tank would overflow. In these cases, an altitude valve must be installed on the tank fill line to keep the tank from overflowing.
| Which is the main purpose(s) of the meter yoke? a. Cushion against stress b. Cushion against stress and strain c. Provide electrical conductivity d. Proper alignment and support for meter | d | Proper alignment and support for meter | Water Transmission and Distribution | 10 | 250 | Many water utilities use a special device called a meter yoke or horn to simplify the installation of small meters. Figure 10-9 illustrates several types that are commonly used for both interior and meter-pit installations. The purpose of a yoke is to hold the stub ends of the pipe in proper alignment and to maintain spacing to support the meter. Yokes also cushion the meter against stress and strain in the pipe and provide electrical continuity when metal pipe is used.
| The minimum cover over a water main below a road in a warm climate with no possibility of frost is a. 2.0 feet. b. 2.5 feet. c. 3.0 feet. d. 3.5 feet. | b | 2.5 feet. | Water Transmission and Distribution | 12 | 310 | In warmer climates where there is no frost, pipe must still have a minimum amount of cover to protect it from damage. This cover will also protect the pipe from highway wheel loads and other impact loads at the surface. The minimum required cover is usually 2.5 ft (0.8 m) for mains and 18 in. (0.5 m) for services.
| The minimum cover over a water service below a road in a warm climate with no possibility of frost is a. 12 inches. b. 18 inches. c. 24 inches. d. 30 inches. | b | 18 inches | Water Transmission and Distribution | 12 | 310 | In warmer climates where there is no frost, pipe must still have a minimum amount of cover to protect it from damage. This cover will also protect the pipe from highway wheel loads and other impact loads at the surface. The minimum required cover is usually 2.5 ft (0.8 m) for mains and 18 in. (0.5 m) for services.
| How far should the excavation extend ahead of the pipe laying? a. 2 pipe lengths b. 3 pipe lengths c. 4 pipe lengths d. Just ahead of the pipe installation | d | Just ahead of the pipe installation | Water Transmission and Distribution | 12 | 310 | In warmer climates where there is no frost, pipe must still have a minimum amount of cover to protect it from damage. This cover will also protect the pipe from highway wheel loads and other impact loads at the surface. The minimum required cover is usually 2.5 ft (0.8 m) for mains and 18 in. (0.5 m) for services.
| Contractors find it easier to lay pipe with the bells facing uphill when the main is being laid on a slope steeper than a. 6%. b. 9%. c. 10%. d. 12%. | a | 6%. | Water Transmission and Distribution | 12 | 324 | Pipe that is joined by couplings may be laid in either direction. Bell-end pipe is normally laid with the bells facing the direction in which the work progresses; however, this approach is not mandatory. When a main is being laid on a slope steeper than 6 percent, contractors often find it is easier to lay the pipe with the bells facing uphill
86 | Which is the best mechanical compacting equipment for clays, tills, and silts? a. Hand-controlled plate tampers b. Vibratory compactors c. Irregular drum tampers d. Boom-mounted plate tampers | c | Irregular drum tampers | Water Transmission and Distribution | 13 | 346 | Irregular drum tampers are used for clays, tills, and silts.
| Which is the best mechanical compacting equipment for sand in shallow lifts? a. Hand-controlled plate tampers b. Vibratory compactors c. Irregular drum tampers d. Boom-mounted plate tampers | a | Hand-controlled plate tampers | Water Transmission and Distribution | 13 | 346 | Hand-controlled plate tampers (Figure 13-3) are used for sand in shallow lifts.
| What is the inlet thread on a standard AWWA corporation stop called? a. Tapered Milwaukee thread b. Minneapolis thread c. Connelly thread d. Mueller thread | d | Mueller thread | Water Transmission and Distribution | 15 | 416 | Corporation stops are available in many different sizes and styles, including several combinations of threads and connections for the inlet and outlet ends. The inlet thread on the standard AWWA corporation stop is the one most commonly used. It is commonly known as the Mueller thread.
| If special bedding material is required by the design engineer due to poor local soil conditions, the material should not contain more than _______ clay or silt that can be sensitive to water. a. 5% b. 10% c. 12% d. 18% | c | 12% | Water Transmission and Distribution | 12 | 322 | If special bedding material is required, it should be a clean, well-graded, granular material up to 1 in. (25 mm) in size. It should contain no lumps or frozen ground and have no more than 12 percent clay or silt that can be sensitive to water. The bedding material should be spread over the trench bottom to the full width of the trench.
| When pipe cannot be structurally supported by natural trench bedding due to very soft soils, 12-24 inches of additional soil should be removed and coarse granular material in well-mixed sizes up to 3 inches used as backfill and placed on top of the geotextile fabric a. True b. False | a | 12 to 24 inches; 3 inches | Water Transmission and Distribution | 12 | 322 | When natural trench bedding is unable to structurally support the pipe, such as in very soft soils, it may be necessary to dig an extra 12 to 24 in. (300 to 600 mm) deeper. Then coarse granular material in well-mixed sizes up to 3 in. (75 mm) can be used as backfill on top of geotextile fabric.
| Who should be contacted to ensure proper disposal of groundwater from a pipe trenching project? a. US Environmental Protection Agency b. Bureau of Land Management, Water Division c. Local regulatory agency d. Local city government or landowner | c | Local regulatory agency | Water Transmission and Distribution | 12 | 314 | It is important to check with local regulatory agencies to ensure proper disposal of the pumped water
| Which is the bolt torque for a mechanical-joint on a standard 48-inch ductile-iron water main? a. 45 to 60 ft-lb b. 120 to 150 ft-lb c. 225 to 250 ft-lb d. 275 to 325 ft-lb | b | 120 to 150 ft-lb | Water Transmission and Distribution | 12 | 330 | Table 12-4
| Cleaning by the air-purging process is used on water mains that are a. 4 inches or smaller. b. 6 inches or smaller. c. 8 inches or smaller. d. 10 inches or smaller. | a | 4 inches or smaller. | Water Transmission and Distribution | 14 | 388 | Air purging. In the air-purging process, air mixed with water is used to clean mains. Generally, small mains, up to 4 in. (100 mm) in diameter, are cleaned using this procedure; however, some utilities have reported using this process for larger mains. Before the procedure is performed, all services must be shut off. Air from a compressor is then forced into the upstream end of a main after the blowoff valve is opened at the downstream end. Spurts of the air–water mixture remove all but the toughest scale
| Fuel oil will permeate which type of pipe? a. Lead pipe b. Polyethylene pipe c. Copper pipe d. Galvanized pipe | b | Polyethylene pipe | Water Transmission and Distribution | 15 | 415 | Plastic tubing must not be used at any location where gasoline, fuel oil, or industrial solvents have contaminated the soil or could do so in the future. Not only will these substances soften the plastic and cause it to eventually fail, but low concentrations will pass through the plastic walls by a process known as permeation.
| Which type of pipe joint is used primarily in exposed locations? a. Mechanical joint b. Flanged joint c. Restrained joint d. Shouldered joint | b | Flanged joint | Water Transmission and Distribution | 2 | 29 | . They are primarily used in exposed locations where rigidity, self-restraint, and tightness are required, such as inside treatment plants and pump stations
| Which type of pipe joint lacks flexibility and thus should not normally be buried? a. Mechanical joint b. Flanged joint c. Restrained joint d. Shouldered joint | b | Flanged joint | Water Transmission and Distribution | 2 | 29 | Flanged joints should not normally be used for buried pipe because of their lack of flexibility to compensate for ground movement
| Which type of pipe joint is most commonly used for river crossings? a. Ball and socket joint b. Shouldered joint c. Push-on joint d. Expansion joint | a | Ball and socket joint | Water Transmission and Distribution | 2 | 29 | Ball-and-socket joints are special-purpose joints, most commonly used for intakes and river crossings.
| Ball and socket joints can provide deflections of up to a. 10.0 degrees. b. 13.0 degrees. c. 15.0 degrees. d. 17.5 degrees. | c | 15.0 degrees | Water Transmission and Distribution | 2 | 29 | Their great advantages are that they provide for a large deflection (up to 15°)
| What is the maximum joint deflection for full lengths of standard 48-inch ductileiron push-joint pipe? a. 3 degrees b. 6 degrees c. 8 degrees d. 10 degrees | a | 3 degrees | Water Transmission and Distribution | 12 | 327 | Table 12-3
| Large meters are usually tested at which percentage of their operating range? a. 5 to 10% b. 10 to 20% c. 20 to 25% d. 25 to 33% | a | 5 to 10% | Water Transmission and Distribution | 10 | 261 | Some water suppliers do not field-test large meters over their entire operating range. Instead they check only the lower 5 to 10 percent of the rated or operating range. Utilities may take this approach because the large quantities of water discharged in high-flow tests often present a problem
| Which one of the following types of pipe is most prone to sliding out of a push-on joint if not firmly restrained? a. Asbestos-cement pipe b. Plastic pipe c. Ductile-iron pipe d. Cast-iron pipe | b | Plastic pipe | Water Transmission and Distribution | 12 | 337 | Plastic pipe has a particularly smooth surface. It is especially prone to sliding out of a push-on joint if not firmly restrained
| The lantern ring is also known as the a. packing ring. b. seal cage. c. packing seal. d. mechanical seal. | b | seal cage. | Water Transmission and Distribution | 3 |  | Pumping: Fundamentals for the Water and Wastewater Maintenance Operator Series. 2001. Frank R. Spellman and Joanne Drinan. Technomic Publishing Company. Chapter 3
| Which is the best mechanical compacting equipment for deep narrow trenches? a. Hand-controlled plate tampers b. Vibratory compactors c. Irregular drum tampers d. Boom-mounted plate tampers | d | Boom-mounted plate tampers | Water Transmission and Distribution | 13 | 346 | Boom-mounted plate tampers are used for clays or sands in deep, narrow trenches that prevent workers from going into the trench.
| When the discharge of a velocity pump is blocked, head builds up, typically greater than the pressure generated during pumping. When this occurs, water recirculates within the pump impeller and casing. This flow condition is called a. run-around. b. skirting. c. slip. d. bypass. | c | Slip | Water Transmission and Distribution | 4 | 79 | When the discharge of a velocity pump is blocked, head builds up, typically greater than the pressure generated during pumping. When this occurs, water recirculates within the pump impeller and casing. This flow condition is refferd to as slip
| Which valves can be used to throttle flow for only a short period of time? a. Butterfly valves b. Altitude valves c. Self-actuating valves d. Plug valves | a | Butterfly valves | Water Transmission and Distribution | 4 | 92 | The best valves for throttling are plug, ball, self-actuating, or altitude valves. Butterfly valves can be used for throttling for short periods of time, but extended use may damage them.
| Which type of valve operates similar to a diaphragm valve? a. Vacuum relief valve b. Globe valve c. Pressure relief valve d. Butterfly valve | b | Globe valve | Water Transmission and Distribution | 6 | 150 | Diaphragm valves operate similarly to globe valves.
| Which valve can go from fully open to fully closed with ¼ turn? a. Plug valve b. Needle valve c. Globe valve d. Pinch valve | a | Plug valve | Water Transmission and Distribution | 6 | 150 | The two principal types of rotary valves used in water systems are plug valves and ball valves. The movable element in a plug valve (Figure 6-6) is a cylinder-shaped or cone-shaped plug that has a passageway or port through it. It requires a one-quarter turn to move from fully open to fully closed
| Foot valves are a special type of a. relief valve. b. control valve. c. check valve. d. plug valve. | c | check valve. | Water Transmission and Distribution | 6 | 152 | They are commonly used at the discharge of a pump to prevent backflow when the power is turned off. Foot valves are a special type of check valve installed at the bottom of the pump suction so that the pump will not lose its prime when power is turned off.
| Usually, which type of hydrant is a flush hydrant? a. Warm-climate hydrant b. Wet-barrel hydrant c. Dry-barrel hydrant d. Standpipe-barrel hydrant | c | Dry-barrel hydrant | Water Transmission and Distribution | 7 | 170 | Flush hydrants are usually of the dry-barrel type.
112 | Which type of temperature sensor uses two wires of different materials? a. Thermistors b. Thermo-resistors c. Thermocouples d. Thermo-conductors | c | Thermocouples | Water Transmission and Distribution | 9 | 217 | Thermocouples use two wires of different materials, represented as metal A and metal B in Figure 9-4A. These wires are joined together at two points: the sensing point and the reference junction. Temperature changes between the two points cause a voltage to be generated, which can be read out directly or amplified through a transducer.
| Which type of temperature sensor uses a semi-conductive material? a. Thermistors b. Thermo-resistors c. Thermocouples d. Thermo-conductors | a | Thermistors | Water Transmission and Distribution | 9 | 217 | Thermistors (Figure 9-4B), also called resistance temperature devices, use a semiconductive material, such as cobalt oxide, that is compressed into a desired shape from the powder form. The material is then heat-treated to form crystals to which wires are attached. Temperature changes are reflected by a corresponding change in resistance of the thermistor, as measured through the attached wires.
| Which is the most frequent cause of hydraulic transients in water distribution systems? a. Controlled pump shutdown b. Flow demand changes c. Pump startup d. Valve opening and closing | d | Valve opening and closing | Water Transmission and Distribution | 5 | 129 | Causes of hydraulic transients in water distribution systems include: (1) valve opening and closing (frequently occurs), (2) flow demand changes (rarely occurs), (3) controlled pump shutdown (rarely occurs), (4) pump failure (often occurs), (5) pump startup (rarely occurs), (6) air-venting from lines (frequently occurs), (7) failure of flow on pressure regulation (rarely occurs), (8) pipe rupture (rarely occurs) (Bosserman and Hunt 1998). Pipelines and distribution systems can be subject to surges very frequently and in many cases almost daily. Over time, this can cause damage to the pipeline and equipment.
| Which type of valve should be used for filling an elevated tank if full system pressure would overflow the tank? a. Pressure-relief valve b. Altitude valve c. Pressure-reducing valve d. Globe valve | b | Altitude valve | Water Transmission and Distribution | 6 |  | Altitude Valve- This type of valve is designed to let the reservoir fill at a regulated rate and to stop flow completely when the tank is full. Altitude valves are also used to control flow to an elevated tank when the tank is not high enough to accept full system pressure
| One form of a differential-pressure flow meter is a(n) a. propeller. b. proportional. c. velocity-type. d. orifice plate. | d | orifice plate. | Water Transmission and Distribution | 9 | 210 | The measurement devices most commonly used for measuring large quantities of water are differential-pressure flowmeters (also called head meters). Their popularity is largely due to a combination of flexibility, simplicity, ease of installation, and reliability. The flow reading of a differential-pressure meter is calculated from the difference between two pressures measured in the meter. Differential-pressure flowmeters are available in many forms, such as the Venturi, modified Venturi, flow tube, or orifice plate.
| Pressure gauges connected to both suction and discharge sides of a pump should be connected a. 2 to 3 feet on either side of a pump, unless there is a change in direction it can go closer. b. 1 foot and 2 feet from the pump on the suction side and discharge side, respectively. c. next to the pump on the suction side and just before the check valve on the discharge valve. d. to the pressure taps supplied on the pump. | d | to the pressure taps supplied on the pump. | Water Transmission and Distribution | 4 | 92 | Pressure gauges should be connected to both the suction and discharge sides of a pump at the pressure taps supplied on the pump.
| Which are the two principal types of throttling valves? a. Throttling and pressure-reducing valves b. Butterfly and relief valves c. Butterfly and altitude valves d. Pressure-reducing and altitude valves | d | Pressure-reducing and altitude valves | Water Transmission and Distribution | 6 | 138-139 | The two principal types of throttling valves used in a water system are pressure-reducing valves and altitude valves.
| Which valve would be best to use to precisely throttle flow? a. Globe valve b. Butterfly valve c. Rotary valve d. Needle valve | d | Needle valve | Water Transmission and Distribution | 6 | 150 | Needle valves are available only in small sizes and are primarily used for precise throttling of flow.
| SCADA systems consist of the following distinct components: a. Remote terminal units (RTUs), communications, and human machine interface (HMI) b. Sensing instrument, RTUs, communications, and HMI c. Sensing instrument, RTUs, communications, master station, and HMI d. RTUs, communications, master station, and HMI | d | RTU’s, communications, master station, and HMI | Water Transmission and Distribution | 9 | 235 | Remote terminal units (RTUs), communications (telemetry transmission), a master station, Human–Machine Interface HMI (through graphical format at a central console).
| Stray-current corrosion is caused by a. corrosive soils. b. acidic soils. c. AC currents. d. DC currents. | d | DC currents | Water Transmission and Distribution | 14 |  | Stray-current corrosion is caused by DC current that leaves its intended circuit, collects on a pipeline, and discharges into the soil.
| Which system would provide for a “soft start” to a motor? a. Wound-rotor induction motor and a controller b. Synchronous motor and a variable frequency controller c. A variable frequency drive and a squirrel-cage induction motor d. Squirrel-cage induction drive and a variable frequency drive | a | Wound-rotor induction motor and a controller | Water Transmission and Distribution | 8 | 185 | The use of variable-frequency drives for pumping applications incorporates a basic wound-rotor induction motor and a controller that modulates the current to the motor. Because the power is not constant, the motor runs at less than full speed, depending on how the power level is selected for the pump speed. If the level is set and the unit starts on a command from a controller, the motor slowly powers up until it reaches its preset speed. This provides a “soft start” to the motor, which reduces the starting current required as compared with a standard motor.
| Which type of relay is frequently used to detect power loss and initiate a switchover to another power source? a. Loss-of-phase relays b. Voltage relays c. Frequency relays d. Circuit breaker relays | b | Voltage relays | Water Transmission and Distribution | 8 | 191 | Voltage relays are frequently used to detect a loss of power and to initiate a switchover to an alternate power source. Under-voltage relays are also used to shut down motors if the voltage drops too low.
| Which type of relays are placed on each phase of a power supply to open up a control circuit and stop a motor, if the current becomes excessive? a. Thermal-overload relays b. Frequency relays c. Voltage relays d. Differential relays | a | Thermal-overload relays | Water Transmission and Distribution | 8 | 191 | Thermal-overload relays are provided on starters to prevent the pump motor from burning out if abnormal operating conditions increase the load beyond the pump’s design capacity. When current is excessive, the relays (sometimes called heaters) placed on each phase of the power supply open the control circuit and stop the motor. These relays are normally set to stop the motor when current exceeds the design load by 25 percent.
| Which type of relay is often used where local power generation is involved and on synchronous motor starters to sense when the motor has reached synchronizing speed? a. Speed sensor relay b. Differential relay c. Frequency relay d. Voltage relay | c | Frequency relay | Water Transmission and Distribution | 8 | 191-192 | Frequency relays respond to changes in the frequency (in cycles per second) of an AC power supply. They are most often used where local power generation is involved. Frequencyrelays are also used on synchronous motor starters to sense when the motor has reached synchronizing speed.
| Which type of relay is frequently used on large equipment to check whether all the current entering a system comes back out of the system? a. Voltage relay b. Over-current relay c. Reverse-current relay d. Differential relay current entering a system comes back out of the system? | d | Differential relay | Water Transmission and Distribution | 8 | 192 | Differential relays are frequently used on large equipment or switchgear. These units check whether all of the current entering a system comes back out of the system. If it does not, the relay closes a contact that shuts down the equipment. An equipment shutdown by a differential relay indicates major trouble, so an electrician should always be called
| Which is the correct sequence of a telemetry signal? a. Indicator, sensor, transmission channel, receiver, transmitter, and signal b. Sensor, transmitter, transmission channel, receiver, and indicator c. Signal, indicator, transmitter, transmission channel, receiver, and sensor d. Signal, sensor, transmission channel, transmitter, receiver, and indicator | b | Sensor, transmitter, transmission channel, receiver, and indicator | Water Transmission and Distribution | 9
| Sacrificial anodes are also called a. corrosion anodes. b. corrosion cells. c. galvanic anodes. d. decaying anodes. | c | galvanic anodes | Water Transmission and Distribution | 14 | 403 | Sacrificial anodes, also called galvanic anodes, consist of magnesium-alloy or zinc castings that are connected to the pipe through insulated lead wires, as shown in Figure 14-19. Magnesium and zinc are anodic to steel and iron, so a galvanic cell is formed that works opposite to the corrosion being prevented. As a result, the magnesium or zinc castings corrode (sacrifice their metal), and the pipe, acting as a cathode, is protected.
| Which is becoming the most common, and is one of the least dangerous, methods of thawing a water service line? a. Hot water b. Electrical c. Small torch d. Steam vibration | a | Hot water | Water Transmission and Distribution | 15 | 425 | Hot-water thawing (Figure 15-15) is becoming more common because it is less dangerous than electrical thawing. In addition, it can be used for plastic pipe. The technique typically involves pumping hot water through a small flexible tube that is fed into the frozen service line.
| When a control switch operated by pressure changes is located too close to a pump station, erratic operation can occur. This problem is known as a. pulsing. b. seesaw arching. c. racking. d. roaming. | c | racking. | Water Transmission and Distribution | 8 | 189 | If the control switch is operated by pressure changes close to the pumping station, erratic operation (known as racking or seeking) can be a problem. Racking occurs when the pressure surge resulting from pump startup immediately causes the pump control pressure switch to shut the pump off again. For this reason, pump operation is often controlled based on pressure changes measured at an elevated storage tank.
| Which is the electronic standard range? a. 4 to 20 mA DC b. 4 to 20 mA AC c. 0 to 100% d. 0 to 1 binary | a | 4 to 20 mA DC | Water Transmission and Distribution | 9 | 223 | As development and usage have progressed, both systems have also standardized signal levels. The pneumatic standard range is 3–15 psig (20–100 kPa [gauge]), whereas the electronic standard is 4–20 mA DC. The practical advantage of this standardization is that control room instruments’ operating mechanisms are based on common signal units in all locations.
| How much resistance should motor-winding insulation exhibit? a. At least 0.5 megohm of resistance b. At least 1.0 megohm of resistance c. At least 2.0 megohm of resistance d. At least 5.0 megohm of resistance | b | At least 1.0 megohm of resistance | Water Transmission and Distribution | 8 | 197 | Motor-winding insulation should be checked periodically to make sure it remains uncontaminated with oil, grease, or moisture. In general, insulation should exhibit at least 1 megohm of resistance
| Which is the pneumatic standard range? a. 0 to 10 psig b. 3 to 15 psig c. 4 to 20 psig d. 0 to 100% | b | 3 to 15 psig | Water Transmission and Distribution | 9 | 223 | As development and usage have progressed, both systems have also standardized signal levels. The pneumatic standard range is 3–15 psig (20–100 kPa [gauge]), whereas the electronic standard is 4–20 mA DC. The practical advantage of this standardization is that control room instruments’ operating mechanisms are based on common signal units in all locations.
| Which of the following methods for preventing external corrosion is only a shortterm remedy? a. Extra thickness for pipe walls b. Wrapping pipe in polyethylene plastic sleeves c. Applying a coating of bitumastic or coal tar d. Installing cathodic protection on the pipe | a | Extra thickness for pipe walls | Water Transmission and Distribution | 14 | 403 | Adding extra thickness to a pipe as a corrosion allowance is not an effective long-term remedy. Pipe corrosion is not uniform. Specifying a corrosion allowance for buried pipe only postpones the problem. Corrosion-prevention methods are much more cost effective.
| The D’Arsonval meter is a. an amperometric meter. b. a type of pH meter. c. an analog (uses a needle) meter. d. a digital (number displays on unit) meter. | c | an analog (uses a needle) meter. | Water Transmission and Distribution | Glossary
| If an excavation on a road requires that one of the lanes be closed and the speed limit is 25 mph, how many cones are required to divert the traffic? a. 6 b. 9 c. 13 d. 15 | a | 6 | Water Transmission and Distribution | 13 | 357-358 | Table 13-5
| If an excavation on a road requires that one of the lanes be closed and the speed limit is 45 mph, how many cones are required to divert the traffic? a. 9 b. 13 c. 15 d. 18 | b | 13 | Water Transmission and Distribution | 13 | 357-358 | Table 13-5
| The prevention of trench cave-ins using the sloping method requires which slope ratio? (Note: horizontal to vertical distance, respectively) a. 1.0 : 1.0 b. 1.5 : 1.0 c. 2.0 : 1.0 d. The angle will vary with type of soil, moisture content, and surrounding conditions | d | The angle will vary with type of soil, moisture content, and surrounding conditions | Water Transmission and Distribution | 12 | 317 | Shoring, if properly installed, will actually prevent the caving in of trench walls. It is basically a framework support system of wood, metal, or both that maintains pressure against both trench walls. It is important that the type and condition of the soil be checked before excavation begins. This allows the correct shoring to be selected. The type and condition of the soil also need to be checked for changes as construction progresses. Soil conditions can vary greatly within a few feet, and conditions may also be changed by weather or vibration.
| If a main cannot be installed at an adequate depth in a cold weather climate, Styrofoam insulation board can be used to protect the water in the pipe from freezing. How far above the pipe should this insulation be installed? a. 2 to 4 inches b. 5 to 7 inches c. 8 to 10 inches d. 1 foot | a | 2 to 4 inches | Water Transmission and Distribution | 12 | 310 | If adequate depth is not possible, a main may be insulated. Closed-cell Styrofoam insulation board, 2 in. (50 mm) thick and 2 to 4 ft (0.6 to 1.2 m) wide, works well. The insulation should be placed on stable fill, a few inches above the pipe, for as long a distance as necessary. Bead-board-type sheets should not be used. They are less expensive, but they have low insulating value and will absorb water, thereby further reducing their effectiveness.
| How much deeper below the grade line of a pipe bottom should a trench be excavated if it is being dug in a rock formation? a. 3 to 6 inches b. 6 to 9 inches c. 9 to 12 inches d. 12 to 18 inches | b | 6 to 9 inches | Water Transmission and Distribution | 12 | 313 | The term rock generally applies to solid rock, ledge rock such as hardpan or shale, and loose boulders more than 8 in. (200 mm) in diameter. In any type of rock formation, the rock must be excavated to a level 6 to 9 in. (150 to 230 mm) below the grade line of the pipe bottom. Proper bedding material must then be added for pipe support. Excavated rock should be hauled away and not used for backfill.
| Pressure-relief valves are most similar to a. globe valves. b. vacuum relief valves. c. needle valves. d. check valves. | a | globe valves | Water Transmission and Distribution | 6 | 150 | Pressure-relief valves are similar to globe valves, but their disks are normally maintained against the seat by a spring
| Current meters are primarily used for measuring flow in lines that are a. 5/8 to 1 inch. b. 1 to 3 inches. c. 3 inches or greater. d. 12 inches or greater | c | 3 inches or greater | Water Transmission and Distribution | 10 | 263 | Current meters Current meters are also commonly called velocity meters. They are principally used to measure flow in lines that are 3 in. (76 mm) and larger. The principal types include turbine, multijet, and propeller meters.
| Which does beam breakage resemble? a. Shear breakage b. Stress breakage c. Flexural breakage d. Tensile breakage | a | Shear breakage | Water Transmission and Distribution | 2 | 19 | Beam breakage, which resembles a shear break, may occur when a pipe is unevenly supported along its length
CH 1 | Which agency sets legal limits on the concentration levels of harmful contaminants in potable water distributed to customers a. National Primary Drinking Water Regulations Agency b.US Environmental Protection Agency c. US public Health Service d. Occupational Health and Safety Administration | a | United States Environmental Protection Agency | Water Distribution Grades 1&2 |  | 2 | The SDWA delegates responsibility for administering the provisions of the to the US Environmental Protection Agency (USEPA). Some principal duties of the agency are as follows: 1.Set maximum allowable concentrations for contaminants that might present a health threat in drinking water. These limits are called main contaminant levels (MCLs). 2. Delegate primary enforcement responsibility for local administration d' requirements to state agencies. 3. Provide grant funds to the states to assist them in operating the greatly expanded program mandated by the federal requirements. 4. Monitor state activities to ensure that all water systems are being are being required to meet federal requirments 5.Provide continued research on drinking water contaminants and improvment of Treatment methods
| The number of monthly distribution system bacteriological samples required is a. Based on the water withdrawal permit b. Based on system size c. Based on population d. Different for each state | c | Based on population served | Water Distribution Grades 1&2
| What is the maximum contaminant level for total trihalomethanes (TTHM) in the United States a. 0.040 mg/L b. 0.060 mg/L c. 0.08 mg/L d. 0.100 mg/L | c | 0.080 mg/L | Water Distribution Grades 1&2 |  | 12, 13 | Maximum residual disinfectant levels Chlorine (4.0 mg/L), Chloramines (4.0 mg/L), and chlorine dioxide 0.8 mg/l MCLs Trihalomethanes TTHM-0.080 mg/L; Haloacetic acids (HAAS)-0.060 mg/L; and two inorganic DBPs-chlorite (1.0 mg/L.) and bromate (0.010 mg/L) A treatment technique for removal of DBP precursor material (enhanced coagulation)
| Under the Surface Water Treatment Rule, disinfection residuals must be collected at the same location in the distribution system as a. Coliform samples b. Total trihalomethanes c. Disinfection by-Products d. Alkalinity, conductivity, and pH for corrosion studies. | a | coliform samples | Water Distribution Grades 1&2 |  | 14 | Surface Water Treatment Rule (SWTR) Intended to protect the public from exposure to Giardia lamblia. EPA add the Interim Enhanced Surface Water Treatment Rule to include Cryptosporidium. The Long-Term 1 and 2 Enhanced Surface Water Treatment Rules strengthen the requirements for microbial protection of all sizes of water systems.
| Iron can cause “red water” and thus customer complaints when its concentration is above its secondary maximum contaminant level of a. 0.01 mg/L b. 0.05 mg/L c. 0.10 mg/L d. 0.30 mg/L | d | 0.30 mg/L | Water Distribution Grades 1&2 |  | 18 | EPA Website lists National Secondary Drinking Water Regulations (primary and secondary) A National Secondary Drinking Water Regulation is a nonenforceable guide line regarding contaminants that may cause aesthetic effects such as taste, odor and color.
| The goal of the Safe Drinking Water Act is for each _____ to accept primary enforcement responsibility (primacy) for the operation of the state’s drinking water program a. State b. Water treatment plant c. Operator d. Municipality | a | State | Water Distribution Grades 1&2 |  | 2 | The intent of the SDWA is for each state to accept primary enforcement responsibility (primacy) for the operation of the state's drinking water program. The states must establish requirements for public water systems that are at least as stringent as those set by USEPA. In Arkansas the primacy agency is the state health department. USEPA has primacy in any state that has not accepted this role
| What is the objective of the Total Coliform Rule? a. To provide Cryptosporidium protection to new systems b. To ensure safe levels of lead and copper in drinking water c. To protect the public from exposer to Giardia Lamblia and Cryptosporidium d. To promote routine surveillance of distribution system water quality to search for fecal matter and/or disease-causing bacteria | d | To promote routine surveillance of distribution system water quality to search for fecal matter and/or disease-causing bacteria | Water Distribution Grades 1&2 |  | 10, 11 | The objective of the TCR is to promote routine surveillance of distribution system water quality to search for fecal matter and/or disease-causing bacteria. All points in a distribution system cannot be monitored, and complete absence of fecal matter and disease-causing bacteria cannot be guaranteed. The TCR is an attempt to persuade water utilities to implement monitoring programs sufficient to verify that public health is being protected as much as possible, as well as allowing utilities to identify any potential contamination problems in their distribution system. The rule requires monthly sampling at each distribution sampling point.
| Which agency sets standards on the concentration levels of harmful contaminants in drinking water? a. National Primary Drinking Water Regulations Agency b. US Environmental Protection Agency c. US public Health Service d. Occupational Health and Safety Administration | b | US Environmental Protection Agency | Water Distribution Grades 1&2 |  | 2 | The SDWA delegates responsibility for administering the provisions of the act to the US Environmental Protection Agency (USEPA). Some principal duties of the agency are as follows: Set maximum allowable concentrations for contaminants that might pre- sent a health threat in drinking water. These limits are called maximum contaminant levels (MCLs).
| Explain the difference between the different tiers of violations. Which one is the most serious? a. Teir 1 is an acute MCL violation requiring public notification within 24 hours, Tier 2 notification must occur within 30 days, Tier 3 requires notification within 1 year. b. Teir 1 is an acute MCL violation requiring public notification within 1 hour, Tier 2 notification must occur within 24 Hours, Tier 3 requires notification within 1 month. c. Teir 1 is an acute MCL violation requiring public notification immediately, Tier 2 notification must occur that day, Tier 3 requires notification within 1 year. d. Teir 1 is an acute MCL violation does not requiring public notification, Tier 2 notification should occur, Tier 3 requires notification to supervision | a | Teir 1 is an acute MCL violation requiring public notification within 24 hours, Tier 2 notification must occure within 30 days, Tier 3 requires notification within 1 year. | Water Distribution Grades 1&2
| A positive E. coli test must be reported to the primacy health agency within what time period? a. 1 hour b. end of shift c. 24 hours d. End of month | c | 24 hours | Water Distribution Grades 1&2 |  | 11 | Positive total coliform samples must be tested for E. coli. If any positive total coliform sample is also positive for E. coli the state must be notified by the end of the day on which the result was received. Repeat samples are required within 24 hours of any total coliform-positive routine sam ple. Three repeat samples are required, one at the site of the positive sample and one within five service taps both upstream and downstream of the positive site. Any positive total coliform samples must be tested for E. coli. Any positive E. col (EC+) samples must be reported by the end of the day. Any positive total coliform (TC+) samples require another set of repeat samples
| How is the required number of monthly bacteriological samples determined? a. Based on the water withdrawal permit b. Based on system size c. Population served d. Different for each state | c | Population served | Water Distribution Grades 1&2
| What is the action level for lead in first-draw samples taken from customer taps? a. 15.0 mg/L b. 0.001 mg/L c. 0.08 mg/L d. 0.015mg/L | d | 0.015 mg/L | Water Distribution Grades 1&2 |  | 16 | The objective of the LCR is to control corrosiveness of the finished water in drinking water distribution systems to limit the amount that may be leached from certain metal pipes and fittings in the distribution system. The action level for lead is 0.015 mg/L, and for copper is 1.3 mg/l.
| A water system is designated as a community public water system if it serves how many homes? a. 15 or more b. At least 5 c. 10 homes more than half a year d. Any number of private residences | a | 15 or more | Water Distribution Grades 1&2 |  | 2 , 3 | 1. Community public water systems serve 15 or more homes. Besides mo pal water utilities, this classification also covers mobile home parks and small homeowner associations that have their own water supply and e more than 15 homes.2.Non-Transient Noncommunity public water systems are establishments that have their own private water systems, serving an average of at least 25 persons who do not live at the location but the same people use the water more than 6 months per year. Examples are schools and factories 3. Transient, noncommunity public water systems are establishments such as parks and motels that have their own water systems and serve an average of at least 25 persons per day, but these persons use the water only occasionally and for short periods of time.
| What authority provides specific water sampling instructions? a. The authorized lab b. US Environmental Protection Agency c. US public Health Service d. The state primacy agency | d | The state Primacy agency | Water Distribution Grades 1&2 |  | 4,5 | WE DO
| According to the Lead and Copper Rule, what is the action level for lead? a. 15.0 mg/L b. 0.001 mg/L c. 0.08 mg/L d. 0.015mg/L | d | 0.015 mg/L | Water Distribution Grades 1&2 |  | 16 | The LCR rule establishes action levels for lead (0.015 mg/L) and copper (1.30 mg/L) for the 90th percentile of the samples measured at customer taps.
| Define Maximum Contaminant Level MCL a. The Maximum recommendation of the level of a contaminant in water as specified in the regulation of the State Health department b. The Minimum acceptable level of a contaminant in water as specified in the regulation of the USEPA c. The Maximum permissible level of a contaminant in water as specified in the regulation of the Safe Drinking Water Act (SDWA) d. The Maximum permissible level of a contaminant in water that can be treated. | c | The Maximum permissible level of a conatminant in water as specifed in the regulation of the Safe Drinking Water Act (SDWA) | Water Distribution Grades 1&2 |  | 2 | The Maximum permissible level of a contaminant in water as specified in the regulation of the Safe Drinking Water Act (SDWA)
| Define Time composite samples. a. A composite sample consisting of several equal-volume samples taken at specific times. b. A composite sample consisting of several different locations taken at specific times. c. A composite sample consisting of several equal-volume samples throughout the month d. A composite sample consisting of several different sample types averaged out. | b | A composite sample consisting of several equal-volume samples taken at specific times. | Water Distribution Grades 1&2 |  | 5 | A composite sample consists of a series of grab samples collected from the same point at different times and mixed together. The composite is then analyzed to obtain the average value. The two types of composite samples commonly used are time composite samples and flow-proportional samples. Time composite samples are made up of equal-volume samples collected at regular intervals Flow-proportional composite samples are also collected at regular time inter vals, but the size of each grab sample is proportional to the flow at the time of sampling,
| Define Flow-proportional composite sample. a. A composite sample in which individual should total the flow rate at the time of the sampling b. A composite sample in which individual sample volumes are proportional to the flow rate at the time of the sampling c. Multiple samples taken at peak flow d. A sample taken when demand is the lowest | b | A composite sample in which individual sample volumes are proportional to the flow rate at the time of the sampling | Water Distribution Grades 1&2 |  | 5 | A composite sample in which individual sample volumes are proportional to the flow rate at the time of the sampling
| Define Maximum Contaminant Limit Goal (MCLG) a. Secondary health-based MCLs b. Goals recommended by the Department of Health c. Nonforcible health-based goals published along with the establishing of an MCL d. Board of Health expectations | c | Nonenforcable health-based goals published along with the establishing of an MCL | Water Distribution Grades 1&2 |  |  | Nonenforcable health-based goals published along with the establishing of an MCL
CH 3 | Domestic water use includes water that is supplied to residential area,_____, and institutional facilities a. Public parks b. Commercial districts c. Industrial facilities d. Municipal buildings | b | commercial districts | Water Distribution Grades 1&2 |  | 69 | commercial districts
| Riparian doctrine is sometimes called "the rule of _______" a. First come first serve b. Reasonable sharing c. Equal use d. Eminent domain | b | reasonable sharing | Water Distribution Grades 1&2 |  | 74 | Riparian doctrine, which is commonly used in the water-rich eastern part of the country, is sometimes called the "rule of reasonable sharing." All states that follow this doctrine subscribe to the basic theory that all property owners who have land abutting a body of water have an equal right to that water.
| During which season is water use typically the highest? a. Winter b. Fall c. Summer d. Autum | c | summer | Water Distribution Grades 1&2 |  | 71 | Water use is typically highest during the summer months when the weather is hot and dry and the need to provide water for exterior activities and landscape irrigation is at its peak.
| Of the common types of distribution systems, which type is considered least desirable? a. Grid b. Tree c. Arterial loop d. collections | b | Tree system | Water Distribution Grades 1&2 |  | 82 | A distributions system is usually designed in 3 different types: Arterial-Loop Grid and Tree System. Tree systems have the most dead ends in their design.
| What type of valves should be provided so that areas within the system can be isolated for repair or maintenance? a. Check valve b. Altitude valve c. Shutoff valve d. Needle Valve | c | Shuttoff Valves | Water Distribution Grades 1&2 |  | 83 | Shutoff valves should be provided so that areas within the system can be isolated for repair or maintenance. To minimize service interruptions, valves should be located at regular intervals and at all branches from the arterial mains.
| T or F Riparian doctrine is A water right that allows the deed holder of the water to sell that water. a. True b. False | b | A water right that allows the owner of land abutting a stream or other natural body of water to use that water | Water Distribution Grades 1&2 |  | 74 | Under riparian doctrine, each riparian property owner can use as much water as needed for any reasonable purpose, as long as this use does not interfere with the reasonable use by other riparian property owners Def of Riparian - relating to or situated on the banks of a river.
| Def- Prior appropriation doctrin | A water right doctrine in which the first user has the right to water befor the subsequent users | A water right doctrine in which the first user has the right to water befor the subsequent users | Water Distribution Grades 1&2 |  | 75 | This doctrin is based on the Idea Priorty in time and Beneficual use.
| Def- Priority in time | The assigning of water rights based on who has been using the longest | The assigning of water rights based on who has been using the longest | Water Distribution Grades 1&2 |  | 75 | Priority In Time is when stream flow is less than what is demanded by all water users along the stream, use is prioritized based on who has been using the water for the longest time. Water withdrawals that began more recently must be discontinued so that withdrawals begun earlier can continue.
| Def- Beneficial use | A water right term indicating that the water is being used for good purposes | A water right term indicating that the water is being used for good purposes | Water Distribution Grades 1&2 |  | 75 | Beneficial Use - a user who has been appropriated water is entitled to it only when it can be used beneficially. Waste is therefore theoretically prohibited, and any available water beyond the amount that can be used by one appropriator is available to others. Furthermore, nonuse of the water for a long period may result in loss of the water right by forfeiture or abandonment
| Def- Absolute ownership | A water right referring to water that is completely owned by one person. | A water right referring to water that is completely owned by one person. | Water Distribution Grades 1&2 |  | 75 | The absolute ownership system is based on the principle that the owner of the land owns everything beneath that land, all the way down to the center of the earth. The dynamic nature of groundwater movement makes it impossible to apply this ownership literally. For all practical purposes, the system is a rule of capture. That is, the landowner can use all the water that can be captured from beneath his or her land.
| Def- Arterial-Loop system | Distribution system layout involving a complete loop of arterial mains around the area being served with branch mains projecting inward (FEW DEAD ENDS) | Distribution system layout involving a complete loop of arterial mains around the area being served with branch mains projecting inward (FEW DEAD ENDS) | Water Distribution Grades 1&2 |  | 82
| Def- Grid system | Distribution system layout in which all ends of the mains are connected. This eliminates dead ends | Distribution system layout in which all ends of the mains are connected. This eliminates dead ends | Water Distribution Grades 1&2 |  | 82
| Def- Tree system | Distribution system layout that centers around a single arterial main which decreases in size and length. Lot of dead ends | Distribution system layout that centers around a single arterial main which decreases in size and length. Lot of dead ends | Water Distribution Grades 1&2 |  | 82
| What is the Hazen-Williams formula | A formula for the Velocity of flow in a pipe | A formula for the Velocity of flow in a pipe | Water Distribution Grades 1&2 |  | 87 | The carrying capacity of pipe depends on a combination of factors, including pipe size, pressure, flow velocity, and head loss resulting from friction. friction loss depends on the pipe roughness ( C-factor), flow velocity, and pipe diameter. The (Refer to the listed Text for Calculations)
CH 4 | The velocity of water is calculated as the quantity of water tha flows through a pipe divided by what a. Divided by the cross-sectional area of the pipe b. Divided by the time the water takes to reach its destination c. Divided by the water’s weight in cubic feet d. Multiplied by resistance to flow | a. | the cross-sectional area of the pipe | Water Distribution Grades 1&2 |  | 90 | Velocity - The speed at which water moves V. Mmeasured in feet per second (ft/sec) or meter per second (m/sec) in metric. The quantity of water or discharge (Q) that flows through a pipe depends on the velocity (V) and the cross-sectional area (A) of the pipe. Mathematically as the formula Q = A x V or V=Q/A Discharge (Q) is how fast the water (V) is moving through how big a pipe (A).
| What is the term for water pressure in a main or in a container that is measured by a guage | Gauge Pressure | Gauge Pressure | Water Distribution Grades 1&2 |  | 92 | When the water pressure in a main or in a container is measured by a gauge the pressure is referred to as gauge pressure. If measured in pounds per square inch, the gauge pressure is expressed as pounds per square inch gauge (psig) Atmosphere, which is equal to approximately 14.7 psi at sea level. Because atmospheric pressure is exerted everywhere not a big factor in water system calculations.
| In hydraulics, how is head measured | Foot-pounds per pound | Foot-pounds per pound | Water Distribution Grades 1&2 |  | 95 | Head is one of the most important measurements in hydraulics. It is used to calculate the hydraulic forces acting in a pipeline and to determine a pump's capacity to overcome or pump against these forces Head is a measurement of the energy possessed by the water at any particular location in the water system, expressed in units of foot-pounds per pound
| What is the term for pressure measured in terms of the height of water (in meters or feet) | Head | Head | Water Distribution Grades 1&2 |  | 95 | When head is expressed in feet, as it normally is, the measurement can always be considered to represent the height of water above some reference elevation. The height of water in feet can also be expressed as pressure in pounds per square inch gauge by dividing the feet-of-water height by 2.31. There are three types of head Pressure head, Elevation head and Velocity head
| What are the three types of head. | Elevation head, Velocity head and pressure head | Elevation head, Velocity head and pressure head | Water Distribution Grades 1&2 |  | 95 | When head is expressed in feet, as it normally is, the measurement can alwaysbe considered to represent the height of water above some reference elevation. The height of water in feet can also be expressed as pressure in pounds per square inch gauge by dividing the feet-of-water height by 2.31. There are three types of head Pressure head, Elevation head and Velocity head.
| pounds per square inch is a measurement of what | Pressure | Pressure | Water Distribution Grades 1&2 |  | 89 | weight based on contact area.
| Def- Hydraulics | The study of fluids in motion or under pressure | The study of fluids in motion or under pressure | Water Distribution Grades 1&2 |  | 89 | The study of fluids in motion or under pressure
| Def- Pressure | The force on a unit area of water | The force on a unit area of water | Water Distribution Grades 1&2 |  | 89 | Water flows in a water system when it is under a force that makes it move, the force on a unit area of water is termed pressure. The pressure in a water system is a measure of the height to which water theoretically will rise in an imaginary standpipe open to atmospheric pressure. The pressure can be static, that is it exists although the water does not flow. Pressure can also be dynamic, existing as "moving energy”.
| Def- Static Pressure | Pressure that exists in water although the water does not flow | Pressure that exists in water although the water does not flow | Water Distribution Grades 1&2 |  | 89 | Water flows in a water system when it is under a force that makes it move, the force on a unit area of water is termed pressure. The pressure in a water system is a measure of the height to which water theoretically will rise in an imaginary standpipe open to atmospheric pressure. The pressure can be static, that is it exists although the water does not flow. Pressure can also be dynamic, existing as "moving energy”.
| Def- Dynamic pressure | Pressure that exists in water as it moves. | Pressure that exists in water as it moves. | Water Distribution Grades 1&2 |  | 89 | Water flows in a water system when it is under a force that makes it move, the force on a unit area of water is termed pressure. The pressure in a water system is a measure of the height to which water theoretically will rise in an imaginary standpipe open to atmospheric pressure. The pressure can be static, that is it exists although the water does not flow. Pressure can also be dynamic, existing as "moving energy”.
| Def- Hydrostatic Pressure | The pressure exerted by water at rest | The pressure exerted by water at rest | Water Distribution Grades 1&2 |  | 89 | If the water in the column is permitted to empty horizontally from the bottom of a column, the water will begin to flow under the hydrostatic pressure applied by the height of the column. The flowing water will have little hydrostatic pressure, but it will have gained moving, dynamic pressure, or kinetic energy. The hydrostatic pressure is static potential energy converted into moving energy
| Def- Velocity (in the context of water) | The Speed / Velocity at which water moves in ft/sec or m/sec | The Speed at which water moves in ft/sec or m/sec | Water Distribution Grades 1&2 |  |  | Velocity The speed at which water moves abbreviated as V. The velocity of water is usually measured in feet per second (ft/sec) in US units and meter per second (m/sec) in metric. The quantity of water or discharge (Q) that flows through a pipe depends on the velocity (V) and the cross-sectional area (A) of the pipe,. Mathematically as the formula Q = A x V or V=Q/A Discharge (Q) is how fast the water (V) is moving through how big a pipe (A).
| What is the formula for Velocity V ( in the context of water) | V= Quanity of water / Cross-sectional area (V=Q/A) | V= Quanity of water / Cross-sectional area (V=Q/A) | Water Distribution Grades 1&2 |  |  | Velocity The speed at which water moves abbreviated as V. The velocity of water is usually measured in feet per second (ft/sec) in US units and meter per second (m/sec) in metric. The quantity of water or discharge (Q) that flows through a pipe depends on the velocity (V) and the cross-sectional area (A) of the pipe,. Mathematically as the formula Q = A x V or V=Q/A Discharge (Q) is how fast the water (V) is moving through how big a pipe (A).
| Def- Head | It is the measurement of energy water has at a certain point in a water system, expressed in feet. It is the measurement of the pressure or force that water exerts. | 1. A measurment of the energy possessed by water at a given location in the water system expressed in feet 2. A measure of the pressure or force exerted by water | Water Distribution Grades 1&2 |  |  | Head is one of the most important measurements in hydraulics. It is used to calculate the hydraulic forces acting in a pipeline and to determine a pump's capacity to overcome or pump against these forces Head is a measurement of the energy possessed by the water at any partic ular location in the water system. In hydraulics, energy (and therefore head) is expressed in units of foot-pounds per pound
| 1 inch squared and 2.31 foot tall column of water creates a pressure of what | 1 psi | 1 psi | Water Distribution Grades 1&2 |  |  | When head is expressed in feet, as it normally is, the measurement can alwaysbe considered to represent the height of water above some reference elevation. The height of water in feet can also be expressed as pressure in pounds per square inch gauge by dividing the feet-of-water height by 2.31. There are three types of head Pressure head, Elevation head and Velocity head.
| Def- Pressure Head | A measurement of the amount of energy in water due to water pressure. | A measurement of the amount of energy in water due to water pressure. | Water Distribution Grades 1&2 |  | 95 | Pressure head is a measurement of the amount of energy in water due to water pressure. The height above the pipeline to which water will rise in a tube exposed to atmospheric pressure ( A piezometer). The water pressure is easily measured by a pressure gauge, and the resulting pressure reading in pounds per square inch gauge may then be converted to pressure head in feet.Pressure head describes the vertical distance from the point of pressure measurement to the hydraulic grade line (HGL)
| Def- Hydraulic grade line(HGL) | It is a line that shows the height water would rise to at different points along a pipe. | A line indicating the piezometric level of water at all points along a conduit. | Water Distribution Grades 1&2 |  |  | A line indicating the piezometric level of water at all points along a conduit. Google it look at images
| Def- Elevation Head | It is the energy water has because of how high it is above a certain point. | The energy possessed per unit weight of a fluid because of its elevation above some refrence point | Water Distribution Grades 1&2 |  | 96 | Elevation head is a measurement of the amount of energy that water possesses because of its elevation. It is measured as the height in feet from some horizontal reference line or benchmark elevation (such as sea level) to the point of interest in the water system. For example, a reservoir located 500 ft above sea level is said to have an elevation head of 500 ft relative to sea level.
| Def- Velocity head | It’s the energy water has because it’s moving — the faster it moves, the more energy it has. | A Measurement of the amount of energy in water due to velocity or motion. | Water Distribution Grades 1&2 |  | 96 | A Measurement of the amount of energy in water due to velocity or motion. The greater the velocity, the greater the energy therfor the greater the velocity head.
Chapter 5 |  |  |  | Water Distribution Grades 1&2
| What is the term for a sudden repeated increase and decrease in pressure that continues until dissipated by friction losses? a. Pipe knocking b. Water hammer c. Pipe Shear d. Beam Brake | b. | Water Hammer | Water Distribution Grades 1&2 |  | 102 | Surge, also known as water hammer, is a sudden repeated increase and a sudden change in water velocity often caused by the opening or closing of valves or hydrants too quickly, or the sudden starting or stopping of pumps due to low power. Water hammer is a transient pressure wave that travels very rapidly throug the pipe and may cause pressure that is several times greater than normal pressure. It can cause extensive damage, such as ruptured pipe and damaged fittings.
| What measurement of a pipe's strengh refers to its ability to withstand the pressure exerted on it after it has been buried in a treanch | External load | External load | Water Distribution Grades 1&2 |  | 101 | External load is the pressure exerted on a pipe after it has been buried in trench. This pressure is a result of the backfill (the material that is filled back into the trench after the pipe has been laid), the traffic load (the weight or impact of the traffic passing over the pipe), and longitudinal thrust loads The pipe must be able to resist a reasonable amount of external damage from impact during installation.
| What term refers to the process by which organic compounds pass through a plastic pipe. | Permeation | Permeation | Water Distribution Grades 1&2 |  | 115 | organic compounds can pass through the walls of plastic pipe, even though the pipe is carrying water under pressure. The process by which the molecules pass through the plastic is called permeation. If gasoline, fuel oil, or other organic compounds have saturated the soil around plastic pipe, a disagreeable taste or odor will often be created in the water. More importantly, the contamination can pose a significant health threat to customers using the water. The organic compounds will also soften the plastic pipe, leading to its eventual failure.Plastic pipes should therefore not be installed in areas where there is known soil contamination by organic compounds.
| What type of cylinder pipe is manufactured by casting mild steel reinforcing cages and a steel cylinder with welded joints within a think concrete core? | Prestressed concrete | Prestressed concrete | Water Distribution Grades 1&2 |  | 117 | Reinforced concrete placed in compression by highly stressed, closely spaced, helicallywound wire. The prestressing permits the concrete to withstand tension forces.
| Def- External load | Any load placed on the outside of the pipe from backfill, traffic, or other sources | Any load placed on the outside of the pipe from backfill, traffic, or other sources | Water Distribution Grades 1&2 |  |  | External load is the pressure exerted on a pipe after it has been buried in a Trench. This pressure is a result of the backfill (the material that is filled back into the trench after the pipe has been laid), the traffic load (the weight or impact of the traffic passing over the pipe), and longitudinal thrust loads.
| Def- Internal Pressure | It’s the pressure of the water inside a pipe. | The hydrostatic pressure within or in a pipe | Water Distribution Grades 1&2 |  | 102 | Internal Pressure is the Hydrostatic pressure within the pipe. Normal water pressure depends on local conditions and requirements but is usuallly in the 400-110psi range
| Def- Water hammer | It’s when water suddenly speeds up or slows down, causing a loud bang or shake in the pipes. | A sudden change in water velocity that creates a bang or shudder. It’s when water suddenly speeds up or slows down, causing a loud bang or shake in the pipes. | Water Distribution Grades 1&2 |  | 102 | The potentially damaging slam, bang, or shudder that occurs in a pipe when a sudden change in water velocity usually as a result of someone too rapidly starting a pump or operating a valve creates a great increase in water pressure
| Def- Tensile strength | It’s how strong a pipe or material is against breaking when pulled from both ends. | A measure of the ability of a pipe or other material ro resisr breakage when it is pilled lengthwise. It’s how strong a pipe or material is against breaking when pulled from both ends. | Water Distribution Grades 1&2 |  | 102 | Pipe strength is expressed in terms of tensile strength and flexural strength Tensile strength is a measure of the resistance a material has to longitudinal, lengthwise, pull before that material fails. Flexural strength is a measure of the ability of a material to bend or flex without breaking. Pipe shear breakage or beam breakage may occur when a force exerted by a pipe causes stresses that exceed the material's tensile or flexural strength. Beam breakage, which resembles a shear break, may occur when a pipe is unevenly supported along its length. A pipe that is resting on a rock, for instance, may break if it is weak in tensile and flexural
| Def- Flexural strength | The ability of a material to bend (Flex) without breaking | The ability of a material to bend (Flex) without breaking | Water Distribution Grades 1&2 |  | 102 | Pipe strength is expressed in terms of tensile strength and flexural strength Tensile strength is a measure of the resistance a material has to longitudinal, lengthwise, pull before that material fails. Flexural strength is a measure of the ability of a material to bend or flex without breaking. Pipe shear breakage or beam breakage may occur when a force exerted by a pipe causes stresses that exceed the material's tensile or flexural strength. Shear break occurs when the earth shifts. Beam breakage, which resembles a shear break, may occur when a pipe is unevenly supported along its length. A pipe that is resting on a rock, for instance, may break if it is weak in tensile and flexural
| Def- Tuberculation | Nodules grow inside pipes, making the inside smaller and the pipe rougher | The growth of nodules on the pipes interior, which reduces the inside diameter and increases the pipe roughness | Water Distribution Grades 1&2 |  |  | The C value of a pipe is a measure of the pipe wall's roughness, which determines the extent to which a pipe resists flow because of friction. Higher C values correspond to smoother pipe. Figure 5-2 illustrates the difference between smooth pipe and pipe with an interior surface roughened by tuberculation (the buildup of corrosion products on the pipe walls). Let me know I have a copy you can borrow.
| Def- Flanged joint | A pipe joint where two smooth surfaces are bolted tightly with a gasket between them. | A pipe joint that consists of two machined surfaces that are tightly bolted together with a gasket between them | Water Distribution Grades 1&2 |  |  | Imagine a joint in a Cage
| Def- Machanical joint | A pipe joint for ductile iron pipe that uses bolts, flanges, and a special gasket | A pipe joint for ductile iron pipe that uses bolts, flanges, and a special gasket | Water Distribution Grades 1&2 |  | 110 | Mechanical Joints A mechanical joint is made by bolting a movable follower ring on the spigot to a flange on the bell. The follower ring compresses a rubber gasket to form the seal. . They provide considerable flexibility in the event there is ground settlement after the pipe is installed
| Def- Ball- and -Socket joint | A special pipe joint that can bend a lot (about 15 degrees). | a specuak-ouroose pipe joint that provides for a large deflection (15 degrees) | Water Distribution Grades 1&2 |  | 110 | Ball and Socket Joints most commonly used for intakes and river crossings. Their great advantages are that they provide for a large deflection (up to 15 degrees) and are positively connected so they won't come apart. The large amount of allowable deflection makes this type of joint useful for pipelines laid across mountainous terrain.
| Def- push- on joint | A pipe joint with a bell-shaped end that holds a rubber ring gasket; the other end is shaped to slide in without tearing the gasket. | A pipe joint consisting of a bell with a specially designed recess to accept a rubber ring gasket. The spigot end must have a beveled edge so it will slip into the gasket without catching or tearing it. | Water Distribution Grades 1&2 |  | 110 | The joint consists of a bell with a specially designed recess to accept a rubber ring gasket. The spigot end must have a beveled edge so it will slip into the gasket without catching or tearing it.
Chapter 6 |  |  |  | Water Distribution Grades 1&2
| Which of the following statements is true regarding unloading gaskets? a. Always have gaskets as neat the trench as possible for easy installation b. always store gaskets in a clean, secure location until they are needed c. store gaskets near electrical motors or other operating electrical equipment d. wipe them off and just use themoperating electical equipment d. dont worry just use them. | b | Always store gaskets in a clean,secure location until they are needed. | Water Distribution Grades 1&2 |  | 125 | Gaskets should be be protected from dirt oil excessive heat and sunlight . The sould not be stored near electrical equipment. Always store gaskets in a clean, secure location.
| Wherever a water main crosses a sewer line, the water main should be at least_______ above or below the sewer line. a. 12 in (0.3m) b. 18in (0.45m) c. 24in (0.61m) d.30in (.76m) | b | 18 inches | Water Distribution Grades 1&2 |  | 136 | In general, potable water pipes and sanitary sewers should not be laid in the same trench. Wherever a water main crosses a sewer line, the water main should be at least 18 in. (0.45 m) above or below the sewer line. For 10 (3 either side of the crossing, the sewer line should be made of either (1) dutie plings. If water and sewer lines are parallel to each other, the distance between the iron with mechanical or push-on joints or (2) PVC with mechanical-joint two should be at least 10 ft (3 m). Refer to local or regulatory agency rules for local requirements.
| What is the greatest expense relating to pipe installation? | Excavation | Excavation | Water Distribution Grades 1&2 |  | ch6
| When digging a trench, what is Sloping | It’s a way to stop trench walls from collapsing by digging the sides at an angle so they stay steady. | A method of preventing cave-ins that involves excavating the side of the trench at an angle so the sides will be stable | Water Distribution Grades 1&2 |  | 133 | Sloping Sloping involves excavating the walls of the trench at an angle. For any section of an excavation, there will be a certain angle, called the angle of repose, for which the surrounding earth will not slide or cave back into the trench. The angle varies with the type of soil, the amount of moisture the soil contains, and the surrounding conditions, especially vibration from machinery.
| What is shielding in the context of Trenches | A method to protect workers against cave-ins through the use of a steel box. Open at top and ends that workers can work in. | A method to protect workers against cave-ins through the use of a steel box. Open at top and ends that workers can work in. | Water Distribution Grades 1&2 |  | 133 | Shielding involves the use of a steel box-open at the top, bottom, and ends-that is placed into the ditch so workers can work inside it.. As the work progresses, the protective box is pushed or towed along the trench to provide a constant shield against any caving of the trench walls. This box is also called a trench shield, portable trench box, sand box, or drag shield. The shield is constructed of steel plates and bracing, welded or bolted together.
| What is trench shoring | A framework of wood and or metal constructed against the walls of a trench to prevent caveins | A framework of wood and or metal constructed against the walls of a trench to prevent caveins | Water Distribution Grades 1&2 |  | 134 | Shoring , if properly installed, will actually prevent the caving in of trench walls. It is basically a framework support system of wood, metal, or both that maintains pressure against both trench walls. It is important that the type and condition of the soil be checked before excavation begins. This allows the correct shoring to be selected. The type and condition of the soil also need to be checked for changes as construction progresses. Soil conditions can vary great within a few feet, and conditions may also be changed by weather or vibration. A shoring assembly has three main parts, as illustrated in Figure
| What is thrust in reguards to a water line | A force resulting from water under pressure and in motion | A force resulting from water under pressure and in motion | Water Distribution Grades 1&2 |  | 147 | Water under pressure and water in motion can exert tremendous forces inside a pipeline. The resulting thrust pushes against fittings, valves, and hydrants and can cause joints to leak or pull apart. All tees, bends, reducers, caps, plugs, valves, hydrants, and other fittings that stop flow or change the direction of flow should be restrained or blocked.
| What is a thrust block | A mass of concrete cast in place between a fitting to be anchored against thrust and the undisturbed soil at the side or bottom of the pipe trench. | A mass of concrete cast in place between a fitting to be anchored against thrust and the undisturbed soil at the side or bottom of the pipe trench. | Water Distribution Grades 1&2 |  | 148 | Thrust blocks are masses of concrete that are cast in place between a fitting. Thrust blocks installed for various pipeline bend situations. It's important that the block be centered on the thrust force. The block should also partially cradle the fitting to distribute the force, but it should not cover the joint fittings to distribute the force, but should not cover the joint fitting
| What is a thrust anchor | block of concrete, often a roughly shaped cube, cast in place below a fitting to be anchored against vertical thrust, and tied to the fitting with anchor rods. | block of concrete, often a roughly shaped cube, cast in place below a fitting to be anchored against vertical thrust, and tied to the fitting with anchor rods. | Water Distribution Grades 1&2 |  | 148 | Thrust anchors may be used when a thrust block cannot be used because there is an obstruction or there is no undisturbed soil to block against. They are also used on vertical bends. PLease Refer to AWWA Water Distribution Grades 1 & 2 As illustrated in the typical designs illustrated in Fig.ure 6-31, steel rods connected to relatively massive blocks of concrete restrain the piping bends.
| Where would you use tie rods | Tie rods are frequently used to restrain mechanical-joint fittings that are located close together | Tie rods are frequently used to restrain mechanical-joint fittings that are located close together | Water Distribution Grades 1&2 |  | 148 | Tie rods are frequently used to restrain mechanical-joint fittings that are located close together. As shown in Figure 6-32 ( PLease Refer to AWWA Water Distribution Grades 1 & 2), threaded rods are usually used. Nuts on either side of each joint connection take the place of the mechanical joint bolt that they replace.
| Where would you use a Restraining fitting | locations where other existing utilities or structures are so numerous that thrust blocks are precluded. that thrust blocks are precluded. | locations where other existing utilities or structures are so numerous that thrust blocks are precluded. that thrust blocks are precluded. | Water Distribution Grades 1&2 |  | 148 | Restraining fittings, which make use of clamps and anchor screws.They are particularly useful in locations where other existing utilities or structures are so numerous that thrust blocks are precluded.
Chapter 7
| Which of the following is not generally a process used for compacting the pipe embedment and backfill placed in a trench? a. Tamping b. Vibrating c. Saturating with water d. Sifting | d | Sifting | Water Distribution Grades 1&2 |  | 153 | Compacting The pipe embedment and backfill placed in a trench are generally compacted by a pass of tamping, vibrating, or saturating the soil with water, depending on the ope of soil or material used
| Leakage is defined as the volume of water that must be added to the full pipeline to maintain a specified test pressure within a _____ range. a. 10-psi b. 5-psi c. 3-psi d. 12-psi | b | 5-Psi (34-kPa) | Water Distribution Grades 1&2 |  | 156 | Testing Procedure Leakage is defined as the volume of water that must be added to the full pipeline to maintain a specified test pressure within a 5-psi (34-kPa) range. The w added to the pipeline will be equal to the amount of water that leaks out. This test process assumes, of course, that all air has been expelled from the line. The spec ified test pressure and the allowable leakage for a given length and type of pipe and joint are given in the AWWA standards and manuals.
| Which of the following is not one of the commonly used methods of applying disinfectant? a. Stream method b. Slug method c. Tablet method d. Continuous feed method | a | The Stream method. | Water Distribution Grades 1&2 |  | 160 | The three most commonly used methods of applying disinfectant are the Contiounuous feed, slug and tabket method.
| Under any soil conditions, cave-in protection is required for trenches or excavations _____ deep or more. a. 15 ft (4.6m) b. 10 ft (3.0m) c. 5 ft (1.5m) d. 2 ft (0.6m) | c | 5 ft (1.5 meters) | Water Distribution Grades 1&2 |  | 165 | Trench Safety Trenches can be made safe if proper excavation and shoring rules are follwed and if proper equipment is used. Proper trench shoring cannot be reduced to a standard formula. Each job presents unique problems and must be considered under its own conditions. Under any soil conditions, cave-in protection is required for trenches or excavations 5 ft (1.5 m) deep or more. Where soil is unstable, protection may be necessary in much shallower trenches.
| When disinfecting a new pipeline with calcium hypochlorite tablets or granules, what should the chlorine target be? a. 1.2 mg/L b. 25 mg/L c. 100 mg/L d. .05 mg/L | b | 25 mg/L | Water Distribution Grades 1&2 |  | 161 | With the tablet method, calcium hypochlorite tablets are placed in each section of pipe, in hydrants, and in other appurtenances. These tablets are usually glued to the top of the pipe. The main is then slowly filled with water at a velocity of less than 1 ft/sec (0.3 m/sec) to prevent dislodging the tablets and washing them to the end of the main. The final solution should have a residual of at least 25 mg/l. It should remain in contact with the pipe for a minimum of 24 hours. It is also advisable to occasionally bleed a little water from the system to ensure that chlorinated water is distributed within the pipe.
| How deep should the compacted covering layer be for pipe less than 8 in. (200 mm) in diameter? For pipes larger than 8 in. (200 mm) in diameter? a. 6-12, 12-24 in b. 2-3, 5-6 in c. 1-2, 3-4 ft d. No less than 2 feet | a | 6-12 in, 12-24 in | Water Distribution Grades 1&2 |  | 154 | Tamping The first layer of backfill should be placed equally on both sides of the pipe, joints, waves, and fittings up to the center line of the pipe. Then it should be compacted. This process is sometimes referred to as haunching.
| How much leakage is allowed for a new pipeline test? | Listed in AWWA standards and manuals. | Listed in AWWA standards and manuals. | Water Distribution Grades 1&2 |  |  | Refer to AWWA
| How must a pipeline be prepared before a sample is taken for bacteriological testing? | The pipeline mustbe flushed of chlorinated water and refilled with water from the system. | The pipeline mustbe flushed of chlorinated water and refilled with water from the system. | Water Distribution Grades 1&2 |  |  | After a new pipe has been flushed of chlorinated water and refilled with water on the system, bacteriological tests must be performed. These tests must meet the requirements of the applicable regulatory agencies. Samples must be ana- bad by a certified laboratory, and results of the analysis must show that the samples tested negative (No Coliform Present) before customers are allowed to use it.
| What term refers to the process of repeatedly pushing a pressurized water pipe vertically to near the bottom of the loose fill at intervals along the excavation? | Jetting | Jetting | Water Distribution Grades 1&2 |  |  | A process known as jetting involves repeatedly pushing a pressurized pipe vertically to near the bottom of the loose fill at intervals along the excavation.
| What is the continuous feed method of disinfecting | A method of disinfecting new or repaired mains in which chlorine is continuously added to the water being used to fill the pipe, so that a constant concentration can be maintained. | A method of disinfecting new or repaired mains in which chlorine is continuously added to the water being used to fill the pipe, so that a constant concentration can be maintained. | Water Distribution Grades 1&2 |  | 160 | Water from the distribution system is slowly admitted to the new pipe section while a concentrated chlorine solution is simultaneously forced into the main
| What is the slug method of disinfecting | A high dosage of chlorine is add to a portion of the water used to fill the pipe. This slug of water is allowed to pass through the entire length of pipe being disinfected. | A high dosage of chlorine is add to a portion of the water used to fill the pipe. This slug of water is allowed to pass through the entire length of pipe being disinfected. | Water Distribution Grades 1&2 |  | 161 | The slug method, a long slug of water is fed into the main with a constant dose of chlorine to give it a chlorine concentration of at least 300 mgl. (make the pH is within acceptable range). Water is then slowly bled from the end of the line at a rate that will cause the slug to remain in contact with each point o the pipe for at least 3 hours as it passes through the main. As the slug passes tees, crosses, and hydrants, the adjacent valves must be operated to ensure that any dead-end sections of pipe are disinfected. This method is used primarily for large diameter mains, where continuous feed is impractical.
| What is the tablet method of disinfecting | Calcium hypochlorite tablets are placed in a section of pipe to be disinfected. Water fills and dissolve the tablets. | Calcium hypochlorite tablets are placed in a section of pipe to be disinfected. Water fills and dissolve the tablets. | Water Distribution Grades 1&2 |  | 161 | With the tablet method, calcium hypochlorite tablets are placed in each section of pipe, in hydrants, and in other appurtenances. These tablets are usually glued to the top of the pipe. The main is then slowly filled with water at a velocity of less than 1 ft/sec (0.3 m/sec) to prevent dislodging the tablets and washing them to the end of the main. The final solution should have a residual of at least 25 mg/l. It should remain in contact with the pipe for a minimum of 24 hours. It is also advisable to occasionally bleed a little water from the system to ensure that chlorinated water is distributed within the pipe.
Chapter 8
| Which of the following is not an advantage of installing meters outside in boxes? a. In areas where ground frost is nominal, a meter box can be relatively small, inexpensive, and easy to install. b. If the boxes can always be readily located, meter boxes make meter reading easier because meter readers do not have to enter the building. c. In areas where there is deep frost, meter pits are much more expensive to construct. d. Placing meters outside eliminates the need to enter buildings to replace the meters, which is difficult in some inside locations. | c | In areas where there is deep frost, meter pits are much more expensive to construct. | Water Distribution Grades 1&2 |  | 170 | The following are some complications associated with outdoor meter boxes: contract. In areas where there is deep frost, meter pits are much more expensive to construct. However, many water systems still require meter pits if there is no appropriate location for a meter in a building. Deeper pits often fill with water and must be pumped before the meter can be read. In addition, pit covers are subject to damage if driven over by a heavy vehicle. It is sometimes difficult to locate pits that are covered with snow.
| Other utilities will allow installation of a meter in a crawl space or untility closet as long as 1. The meter can easily be accessed by a meter reader or (2) A. The meter is equipped with a remote reading device B. The homeowner can easily access and report the meter reading C. The meter can self report to the utility D. Water fees are fixed in the area and reading is unnecessary | a | The meter is equipped with a remote reading device. | Water Distribution Grades 1&2 |  | 171 | Water utilities that install meters in basements may be faced with the problem of deciding where to install meters if the buildings only have a crawl space or are constructed on a concrete slab. For these buildings, some utilities require meters to be installed in meter boxes. Other utilities will allow installation in a crawl space or utility closet as long as (1) the meter can easily be accessed by a meter reader or (2) the meter is equipped with a remote reading device.
| What my cause galvanized iron pipe to corrode excessively? | Direct connection to brass and other metal fittings. | Direct connection to brass and other metal fittings. | Water Distribution Grades 1&2 |  | 172 | In some soil, galvanized pipe works fairly well. However, it can fail within year or so under corrosive soil conditions. In addition to general corrosion contact with soil, galvanic corrosion often causes disintegration of the pipe at connection with brass fittings unless dielectric fittings are used
| What is a curb stop used for? | Turning off service for repair or as the result of nonpayment | Turning off service for repair or as the result of nonpayment | Water Distribution Grades 1&2 |  | 174 | When meters are located outside in a meter box, a shutoff valve for use in temporarily shutting off the service is installed in the box on the inlet side of the meter. When meters are located inside, a shutoff valve called a curb valve or curb stop is installed in the service line. The valve is usually located either between the street curb and the sidewalk or on the property line and are used for temporly Turning off service for repair or as the result of nonpayment.
| What is the typical service line size for a single-family residence? | 3/4 inch (19-mm) | 3/4 inch (19-mm) | Water Distribution Grades 1&2
| What is the term for the valve used to connect a small-diameter services line to a water main? | Corporation stop | Corporation stop | Water Distribution Grades 1&2
| What is the generally considered the best location for a tap on main? | At an angle of about 45 degrees down from the top of the pipe. | At an angle of about 45 degrees down from the top of the pipe. | Water Distribution Grades 1&2
| What is a meter box? | A pit-like enclosure that protects water meters installed outside of buildings and allows access for reading the meter | A pit-like enclosure that protects water meters installed outside of buildings and allows access for reading the meter | Water Distribution Grades 1&2
| What is galvanic corrosion? | A form of localized corrosion caused by the connection of two different metals in an electrolyte, such as water | A form of localized corrosion caused by the connection of two different metals in an electrolyte, such as water | Water Distribution Grades 1&2
| What is a corporation stop? | A valve for joining a service line to a street water main. | A valve for joining a service line to a street water main. | Water Distribution Grades 1&2
| What is tapping and what are the two types | The process of connecting laterals and service lines to mains and/ or other laterals. Dry tap (empty) and wet tap (pressurized) | The process of connecting laterals and service lines to mains and/ or other laterals. Dry tap (empty) and wet tap (pressurized) | Water Distribution Grades 1&2
| What is a service saddle? | A device attached around a main to hold the corporation stop. | A device attached around a main to hold the corporation stop. | Water Distribution Grades 1&2
Chapter 9 | Valves
| Which type of valve should be installed at a dead-end water main? A. Vacuum Valve B. Air relief Valve C. Blowoff valve D. Pressure-relief valve | c | Blowoff valve | Water Distribution Grades 1&2
| Which type of valve operates similar to a diaphragm valve? A. Vacuum Valve B. Air relief Valve C. Globe Valve D. Pressure-relief valve | c | Globe valve | Water Distribution Grades 1&2 |  | 187/192 | The globe valve principle is commonly used for water faucets and other house- hold plumbing. As illustrated in Figure 9-6, the valves have a circular disk that moves downward into the valve port to shut off flow. Although they seat very tightly, globe valves produce high head loss when fully open. They are not suited for distribution mains where head loss is critical. Diaphragm valves operate similarly to globe valves. A manually opened water pressure exerted on a diaphragm is used to assist in closing the diaphragm valve
| Which type of valve can go from fully open to fully closed with a quarter turn? a. Plug Valve b. Needle Valve c. Globe Valve d. Pinch Valve | a | Plug valve | Water Distribution Grades 1&2 |  | 187 | In a water utility, a plug valve is used primarily for on/off service and flow diversion rather than precise flow control. It has a cylindrical or conically tapered “plug” with a hole through it. Rotating the plug aligns the hole with the pipeline to allow flow, or turns it perpendicular to stop flow.
| Foot valves are a special type of a. Relief Valve b. Control Valve c. Check Valve d. Plug valve | c | Check Valve | Water Distribution Grades 1&2 |  |  | In a water utility, a foot valve is a type of check valve installed at the inlet of a suction pipe, usually in a well, reservoir, or pump intake. Its main purpose is to allow water to flow into the pump but prevent it from flowing backward, keeping the suction line primed.
| Which type of valve would be best to use to precisely throttle flow? a. Globe Valve b. Butterfly Valve c. Rotary Valve d. Needle valve | d | Needle valve | Water Distribution Grades 1&2 |  |  | In a water utility, a needle valve is used to precisely control the flow rate of water in a system. Unlike regular valves that are mainly “on” or “off,” needle valves have a slender, tapered stem (like a needle) that fits into a matching seat. Turning the valve slowly allows very fine adjustments to the flow.
| Which type of valve is used to isolate a pump on the suction side? a. Butterfly Valve b. Globe Valve c. Gate Valve d. Ball Valve | c | Gate Valve | Water Distribution Grades 1&2 |  |  | In a water utility, a gate valve is primarily used for on/off service—it is not designed for flow regulation. It has a flat or wedge-shaped “gate” inside that moves up and down to open or close the flow path.
| When fully opened, which type of valve will have the highest head loss? a. Gate Valve b. Plug Valve c. Globe Valve d. Ball Valve | c | Globe valve | Water Distribution Grades 1&2 |  | 192 | The globe valve principle is commonly used for water faucets and other house- hold plumbing. As illustrated in Figure 9-6, the valves have a circular disk that moves downward into the valve port to shut off flow. Although they seat very tightly, globe valves produce high head loss when fully open. They are not suited for distribution mains where head loss is critical. Diaphragm valves operate similarly to globe valves. A manually opened water pressure exerted on a diaphragm is used to assist in closing the diaphragm valve
| Which type of valve will prevent the collapse of a pipe? a. Pressure-relief Valve b. Needle Valves c. Pinch Valve d. Air-and-vacuum relief valve | d | Air and vacuum relief | Water Distribution Grades 1&2 |  | 192 | Air-and-vacuum relief valves consist of float-operated valve that will allow air to escape as long as the float is down When water fills the container, the float rises and closes the valve. If trapped or entrained air subsequently enters the unit, the float drops long enough to vent the air and then recloses. If a vacuum occurs in a pipeline, the relief valve will admit air to prevent collapse or buckling of the pipe
| What type of valve is installed at frequent intervals in distribution piping so that small sections of water main may be shut off for maintenance or repair? | Isolation Valve | Isolation Valve | Water Distribution Grades 1&2
| What are the two principal types of throttling valves used in a water system? | Pressure-reducing valve and altitude valve | Pressure-reducing valve and altitude valve | Water Distribution Grades 1&2 |  |  | Throttling the flow of water requires special valve designs that are durable over a long period of time. The two principal types of throttling valves used in system are pressure-reducing valves and altitude valves. It is somtimes necessary to create two or more separate pressure zones in a distribution system in order to furnish all customers with water at an adequate (but not excessive) pressure. The most common way of accomplishing this is to take water from a higher pressure zone and reduce the pressure for the lower zone by using pressure-reducing valves. The valves operate automatically to throttle flow and maintain a lower pressure in the lower distribution system zone. Altitude Valve- this type of valve os desogned to let the reservoir fill at a regulated rate and stop flow completely when the tank is full. Altitude valves are also used to control flow to an elevated tank when the tank is not high enough to accept full system pressure. The valve will automatically shut off flow to the tank to keep the tank from overflowing. Single-acting altitude valves allow water to flow in only one direction. Double-acting valves allow flow in both directions
| What are the three types of power actuators commonly used to operate valves? |  | Electric, Hydraulic and Pneumatic | Water Distribution Grades 1&2 |  | 196
| What is an isolation valve used for | installed in a pipline to shut off flow in portions of the pipe for the purpose of inspection or repairs | installed in a pipline to shut off flow in portions of the pipe for the purpose of inspection or repairs | Water Distribution Grades 1&2 |  | 183 | Isolation valves are installed at frequent intervals in distribution piping so that small sections of water main may be shut off for maintenance or repair. The closer valves are spaced, the fewer the number of customers who will be inconvenienced by having their water turned off while repairs are being made. When a system is laid out in a grid pattern, normal practice is to install at least two valves at each intersection, as illustrated in Figure 9-1. Distribution system valves should mainy be maintained in a fully open position
| What is a pressure reducing valve | A valve with a horizontal disk for automatically reducing water pressure in a main to a preset value | A valve with a horizontal disk for automatically reducing water pressure in a main to a preset value | Water Distribution Grades 1&2 |  |  | It is somtimes necessary to create two or more separate pressure zones in a distribution system in order to furnish all customers with water at an adequate (but not excessive) pressure. The most common way of accomplishing this is to take water from a higher pressure zone and reduce the pressure for the lower zone by using pressure-reducing valves.
| Describe the function of an altitude valve | A valve that automatically shuts off water flow when the water level in an elevated tank reaches a preset elevation (altitude), then opens again when the pressure on the system side is less than that on the tank side. | A valve that automatically shuts off water flow when the water level in an elevated tank reaches a preset elevation (altitude), then opens again when the pressure on the system side is less than that on the tank side. | Water Distribution Grades 1&2 |  |  | Altitude Valve- this type of valve os desogned to let the reservoir fill at a regulated rate and stop flow completely when the tank is full. Altitude valves are also used to control flow to an elevated tank when the tank is not high enough to accept full system pressure. The valve will automatically shut off flow to the tank to keep the tank from overflowing. Single-acting altitude valves allow water to flow in only one direc- tion. Double-acting valves allow flow in both directions
| What is a pressure relief valve? | A valve that opens automatically when the water pressure reaches a preset limit to relieve the stress on a pipe. | A valve that opens automatically when the water pressure reaches a preset limit to relieve the stress on a pipe. | Water Distribution Grades 1&2 |  | 185 | A rapid increase in pressure in a water distribution system is usually called water hammer. The pressure wave that moves rapidly down a pipe can damage valves, burst pipes, or blow pipe joints apart. A common cause of water hammer is opening or closing a valve too fast. Pressure-relief valves can be installed to release some of the energy created by water hammer.
| Where would you find a aire-relief valve and what is it purpose? | An air valve placed at a high point in a pipeline to release air automatucally, thereby preventing air binding and pressure build up. | An air valve placed at a high point in a pipeline to release air automatucally, thereby preventing air binding and pressure build up. | Water Distribution Grades 1&2 |  |  | Air-and-vacuum relief valves consist of float-operated valve that will allow air to escape as long as the float is down When water fills the container, the float rises and closes the valve. If trapped or entrained air subsequently enters the unit, the float drops long enough to vent the air and then recloses. If a vacuum occurs in a pipeline, the relief valve will admit air to prevent collapse or buckling of the pipe
| Describe a gate valve? | A Valve in which the closing element consists of a disc that slides across an opening to stop the flow of water. | A Valve in which the closing element consists of a disc that slides across an opening to stop the flow of water. | Water Distribution Grades 1&2 |  |  | In a water utility, a gate valve is primarily used for on/off service—it is not designed for flow regulation. It has a flat or wedge-shaped “gate” inside that moves up and down to open or close the flow path.
| What is a Bypass valve? | A small valve installed in parallel with a larger valve. Used to equalize the pressure on both sides of the disc of the larger valve befor it is opened. | A small valve installed in parallel with a larger valve. Used to equalize the pressure on both sides of the disc of the larger valve befor it is opened. | Water Distribution Grades 1&2 |  | 189 | Thrusts cause a lot of friction on the valve guides, which makes large gate valves extremely difficult to open. For this reason, bypass valves may be needed. Bypass valves are smaller diameter valves that will allow water to pass around the larger valve. This reduces the differential pressure across the closed disk and the main valve easier to open and close. Bypass valves also provide for flow without the need for opening the main valve.
| What is a cutting-in valve | A specially designed gate valve used with a sleeve that allows the valve to be placed in an existing main. | A specially designed gate valve used with a sleeve that allows the valve to be placed in an existing main. | Water Distribution Grades 1&2 |  | 190 | A cutting in valve has one oversized end connection designed to be used with a cutting in sleeve. The valve and sleeve used together greatly facilitate installation of a new valve in an existing main. Main pressure must be shut off for a period of time to make the installation. This approach is a relatively inexpensive way of adding a valve in a distribution system.
| What is the advantage of a inserting valve | A shutoff valve that can be inserted by a special apparatus into a pipeline whle the line is in service under pressure | A shutoff valve that can be inserted by a special apparatus into a pipeline whle the line is in service under pressure | Water Distribution Grades 1&2 |  | 190 | When it is necessary to install a valve in a water main without shutting off pressure, a special inserting valve can be used . Water utilities normally have an inserting valve installed by a company that has the special equipment required to make the installation and specializes in this work.
| What type of valve is a resilient-seat valve? | A gate valve that’s disk has resilient material attached disigned for leak-tight high pressures. | A gate valve that’s disk has resilient material attached disigned for leak-tight high pressures. | Water Distribution Grades 1&2 |  | 190 | New designs of gate valves are available that use a resilient seat of rubber or synthetic material When the valve is closed, the seat provides a seal between the valve body and the disk. The design offers easier operation and leak-tight shutoff
| A slide valve is a | A gate valve that uses a thin gate that slides up and down where tight shutoff is not important. | A gate valve that uses a thin gate that slides up and down where tight shutoff is not important. | Water Distribution Grades 1&2 |  | 190 | Where the pressure to be regulated is relatively low and tight shutoff is not important, knife gate or sluice gate valves may be used These valves use a relatively thin gate or blade that slides up and down in a recess.
| A globe valve is | A valve having a round, ball like shell and horizontal disk | A valve having a round, ball like shell and horizontal disk | Water Distribution Grades 1&2 |  |  | The globe valve principle is commonly used for water faucets and other house- hold plumbing. As illustrated in Figure 9-6, the valves have a circular disk that moves downward into the valve port to shut off flow. Although they seat very tightly, globe valves produce high head loss when fully open. They are not suited for distribution mains where head loss is critical.
| Needle valves are used for what | Primarily used for precise throttling of flow | Primarily used for precise throttling of flow | Water Distribution Grades 1&2 |  | 191 | In a water utility, a needle valve is used to precisely control the flow rate of water in a system. Unlike regular valves that are mainly “on” or “off,” needle valves have a slender, tapered stem (like a needle) that fits into a matching seat. Turning the valve slowly allows very fine adjustments to the flow.
| What the two functions of an air-and-vacuum relief valve. | 1. Permits entrance of air into a pipe being emptied 2. allows air to escape in a pipe while it is being filled or under pressure | 1. Permits entrance of air into a pipe being emptied 2. allows air to escape in a pipe while it is being filled or under pressure | Water Distribution Grades 1&2 |  |  | These vales consist of a float operated valve that will allow air to escape as long as the float is down. As water fills the container the valve will close. If air is present, the float will be displaced by air and allow to vent.
| How does a pinch valve work | Closes by pinching shut a flexible interior liner | Closes by pinching shut a flexible interior liner | Water Distribution Grades 1&2 |  |  | A Valve will pinch a line there for shutting off of throttling the flow.
| What is a plug valve | A valve in which the movable element is a cylindrical or conical plug. | A valve in which the movable element is a cylindrical or conical plug. | Water Distribution Grades 1&2 |  |  | A rotary type valve with a cylinder or cone shaped valve. Normaly a 1/4 turn can open of close the valve.
| A Ball valve consists of what | A ball with a hole bored through it resting in a cylindrical seat that can close when rotated 90 degrees | A ball with a hole bored through it resting in a cylindrical seat that can close when rotated 90 degrees | Water Distribution Grades 1&2 |  |  | Simalur to a plug valve, but a ball style orifice.
| A butterfly valve consists of what | A valve in which a disc rotates on a shaft as the valve opens or closes. In the fully open position, the disc is parallel to the axis of the pipe. | A valve in which a disc rotates on a shaft as the valve opens or closes. In the fully open position, the disc is parallel to the axis of the pipe. | Water Distribution Grades 1&2 |  |  | Because the disk of the valve stays in the water path in the open position, the valve creates a somewhat higher resistance to flow than does a gate valve. They have the advantage to open faster and easier. This due to water pressure being on both sides of the valve.
| A check valve is designed to do what | A check valve is designed to open in the direction normal flow and close with reversal of flow. | A check valve is designed to open in the direction normal flow and close with reversal of flow. | Water Distribution Grades 1&2 |  |  | These Types of valves are foot valves and used in black flow preventions. The main goal is to ensure flow in one direction, and prevent in flow in the oppsite directions.
| What is an actuator | A device usually electically or pneumatically powered that is used to operate valves. | A device usually electically or pneumatically powered that is used to operate valves. | Water Distribution Grades 1&2
Chapter 10
| Most water systems use hydrants with two_________-diameter nozzles and one _______-diameter nozzle. a. 2.0 inch ;3.0 inch b. 2.0 inch ;4.0 inch c. 2.5 inch ;3.5 inch d. 2.5 inch ;4.5 inch | d | 2.5- inches and 4.5 inches | Water Distribution Grades 1&2 |  | 207 | The outlet nozzles are threaded bronze outlets on the upper barrel. They are used 1) to connect hose lines for direct use of main pressure or (2) to connect a suction hose from the hydrant to the pumper truck. Most water systems with two 2.5-in. (64-mm) nozzles and one 4.5-in. (114-mm) nozzle. The smaller diameter outlet nozzles are for connecting to fire hoses. The larger nozzle, called a pumper outlet or steamer outlet, is used for connecting to a pumper suction hose. Outlet-nozzle threads are normally National American thread
| Miscellaneous use of fire hydrants is a. Is never authorized b. is at the public’s discretion on an as needed basis. c. Is generally discouraged but may be authorized in a controlled context d. Is a useful way of testing hydrants indirectly | c | Is generally discouraged, but my be authotized in a controlled context. | Water Distribution Grades 1&2
| Which of the following is not a common classification of fire hydrants? a. Flow hydrant b. Warm-climate hydrant c. Wet-barrel hydrant d. Dry-barrel hydrant | a | Flow Hydrant | Water Distribution Grades 1&2
| The lower barrel should be buried in the ground so that the connection to the upper barrel is approximately______ above the ground. a. 12 in b. 1 in c. 6 in d. 2 in | d | 2 in | Water Distribution Grades 1&2
| What type of fire hydrant is used in freezing climates? | Dry-Barrell hydrant | Dry-Barrell hydrant | Water Distribution Grades 1&2 |  |  | The have a drain valve that keeps water from being within
| What is and auxiliary valve used for? | Turning off the hydrant for repair or maintenance. | Turning off the hydrant for repair or maintenance. | Water Distribution Grades 1&2 | 10 | 208 | These valves allow th hydrants to be worked on without having to shuttoff the water.
| Why is a fire hydrant operating nut five sided | To prevent operation using a standard socket wrench | To prevent operation using a standard socket wrench | Water Distribution Grades 1&2 |  |  | People be dumb
| In what type of fire hydrant are the the entire barrel and head below ground elevation? | Flush Hydrant | Flush Hydrant | Water Distribution Grades 1&2
| In the standard hydrant color scheme, what color are class A hydrants? | Geen | Green | Water Distribution Grades 1&2 | 10 | 211 | On Page 211 Table 10-1, there is a breakdown pf the different types AA, A, B, C
| What is Fire Flow | The rate of flow measured in gpm that can be delivered from a water distribution system at a special residual pressure for fire fighting. | The rate of flow measured in gpm that can be delivered from a water distribution system at a special residual pressure for fire fighting. | Water Distribution Grades 1&2 | 10 | 203
| In a dry-Barrel hydrant, where is the main valve, and why. | The main valve is located at the base so the hydrant only fills when opened. The hydrant stays dry to prevent freezing. | The main valve is located at the base so the hydrant only fills when opened. The hydrant stays dry to prevent freezing. | Water Distribution Grades 1&2 | 1 | 204 | These Hydrants have a small valve to allow water to drain. The will not freeze and not cause a water leak if damaged.
| What is a breakaway hydrant, and where is it used. | A two part dry barrel designed to break upon imact. Used in traffic areas. | A two part dry barrel designed to break upon imact. Used in traffic areas. | Water Distribution Grades 1&2 | 10 | 205 | These are designed for high Traffic Areas
| What is a wet-barrel hydrant | A Pressurized hydrant with no main valve. Used in non-freezing environments. | A Pressurized hydrant with no main valve. Used in non-freezing environments. | Water Distribution Grades 1&2 | 10 |  | These hydrants are filled with water at all times.
| What is a Flush hydrant | A fire hydrant with the entire barrel and head below ground. Usullay low or flush with the ground. | A fire hydrant with the entire barrel and head below ground. Usullay low or flush with the ground. | Water Distribution Grades 1&2 | 10 | 206 | A standpipe style hydrant that’s is below ground. These are used in area where normal hydrants are not practical such as airport tax iways and high pedestrain areas.
Chapter 11
| The _____ may require the installation of obstruction lights on an elevated tank, depending on its height and location and aircraft in the vicinity. a. ADH b. EPA c. FAA d. AWWA | c | Federal Aviation Administration FAA | Water Distribution Grades 1&2 | 11
| What is the result of utilizing storage to minimize pumping? | More Efficient use of energy and lower operating cost. | More Efficient use of energy and lower operating cost. | Water Distribution Grades 1&2 | 11
| What is the term for a tank that rests on the ground and has a height that is greater than its diameter? | Standpipe | Standpipe | Water Distribution Grades 1&2 | 11
| What is the term for a vertical supply pipe to an elevated tank? | Riser | Riser | Water Distribution Grades 1&2 | 11
| Ponds, lakes, or basins are all examples of what type of raw-water storage container? | Reservior | Reservior | Water Distribution Grades 1&2 | 11
| The height of water in three differently shaped tanks is 22.4 feet. Which tank will have the highest psi at the bottom? a. The square tank b. The rectangular tank c. The cylindrical tank d. It will be the same in all three tanks | d | It will be the same in all three tanks | Water Distribution Grades 1&2 | 11
| Which of the following is the proper detention time for disinfecting a water storage tank that is filled with already chlorinated water such that the free chlorine residual is 10 mg/L after the proper detention time is completed? a. 4 hours b. 6 hours c. 8 hours d. 24 hours | b | 6 hours | Water Distribution Grades 1&2 | 11
| Which of the following is the proper detention time for disinfecting a water storage tank with water that is mixed with hypochlorite already in the tank such that the free chlorine is 10 mg/L after proper detention time is complete? a. 4 hours b. 6 hours c. 8 hours d. 24 hours | d | 24 hours | Water Distribution Grades 1&2 | 11
| In what type of water storage system does water generally “float” on the system? a. Elevated storage b. Demand Storage c. Emergency Storage d. Operating Storage | d | Operating storage. | Water Distribution Grades 1&2 | 11
| What is operating storage? | A tank supplying a given area and capable of storing water demand during low demand, for use when demands exceeds the pumps capacity. | A tank supplying a given area and capable of storing water demand during low demand, for use when demands exceeds the pumps capacity. | Water Distribution Grades 1&2 | 11
| What is emergance storage? | The storage volume reserved for catasrophic situations. | The storage volume reserved for catasrophic situations. | Water Distribution Grades 1&2 | 11
| What is an elevated tank. | A storage tank supported by post or columns rasied above the ground. | A storage tank supported by post or columns rasied above the ground. | Water Distribution Grades 1&2 | 11
| What are the characteristics of a standpipe. | A ground-level water storage tank for which the height is greater than the diameter. | A ground-level water storage tank for which the height is greater than the diameter. | Water Distribution Grades 1&2 | 11
| What is a reservoir? | 1. any tank or basin used for the storage of water 2. A ground level storage tank where the diameter is greater than the height. | 1. any tank or basin used for the storage of water 2. A ground level storage tank where the diameter is greater than the height. | Water Distribution Grades 1&2 | 11
| What is a ground-level tank | A storage tank where the bottom is at or below the surface. | A storage tank where the bottom is at or below the surface. | Water Distribution Grades 1&2 | 11
| What is a hydropneumatic system | An air tank uses compressed air over the water to create pressure in the distribution system. | An air tank uses compressed air over the water to create pressure in the distribution system. | Water Distribution Grades 1&2 | 11
| What is a riser | The vertical supply pipe to an elevated tank. | The vertical supply pipe to an elevated tank. | Water Distribution Grades 1&2 | 11
Chapter 12
| Which basic electrical unit used to measure a material's opposition to the flow of electricity? a. Ampere b. Ohm c. Volt d. Joule | b | Ohm | Water Distribution Grades 1&2
| The D"Arsonval meter is a. An amperometric meter b. A type of pH meter c. An analog (uses a needle meter) d. A digital (numbers displays on units) meter | c | An Analog meter (uses a needle) | Water Distribution Grades 1&2
| Which of the following is not an example of a secondary instrument? a. Telemetery device b. Multiplexing device c. pH monitor d. Indicator | c | pH Monitor | Water Distribution Grades 1&2
| Secondary instrumentation transmits information of what type? | Information provided by sensors | Information provided by sensors | Water Distribution Grades 1&2
| What are the two types of temperature sensors commonly connected to instrumentation? | Thermocouples thermistors | Thermocouples thermistors | Water Distribution Grades 1&2
| In what type of control system is each piece of equipment adjusted by the water system operator directly turning it on and off? | Direct manual control | Direct manual control | Water Distribution Grades 1&2
| What type of automatic control system measures a variable and adjusts the equipment proportionally? | Feedforward proportional control | Feedforward proportional control | Water Distribution Grades 1&2
| Direct current (DC) is current that flows _____________ | Continuously in one direction | Continuously in one direction | Water Distribution Grades 1&2
| Alternating current (AC) is current that____________ | reverses its direction in a periodic manner | reverses its direction in a periodic manner | Water Distribution Grades 1&2
| What is primary and secondary instrumentation | Primary instruments required to operate the monitoring system and secondary displays the information. | Primary instruments required to operate the monitoring system and secondary displays the information. | Water Distribution Grades 1&2
| What is the unit used to measure electrical potential or pressure, where one unit will send a current of 1 ampere through a resistance of 1 ohm? | Voltage | Voltage | Water Distribution Grades 1&2
| In telemetry, what type of signal varies in volts as the measured parameter changes? | Voltage | Voltage | Water Distribution Grades 1&2
| What is the term for the flow rate of electricity, measured in amperes? | Current | Current | Water Distribution Grades 1&2
| What electrical quantity varies in amplitude in telemetry systems to represent changes in a parameter? | Current in telemetry | Current in telemetry | Water Distribution Grades 1&2
| What term describes a circuit characteristic that restricts current flow, similar to friction in a pipeline, and is measured in ohms? | Resistance | Resistance | Water Distribution Grades 1&2
| What is the term for the amount of work done per unit time by an electrical circuit, expressed in watts? | Power | Power | Water Distribution Grades 1&2
| Which device uses a needle and coil of wire in a magnetic field to measure electric current? | D'Arsonval meter | D'Arsonval meter | Water Distribution Grades 1&2
| What instrument is used to measure real power, typically stated in kilowatt-hours (kWh)? | Wattmeter | Wattmeter | Water Distribution Grades 1&2
| What component of an instrument displays information about a monitored system, typically through an analog or digital display? | Indicator | Indicator | Water Distribution Grades 1&2
| What is telemetry | A system of sending data over long distances cpmsisting of a transmitter, a transmission channel and a receiver | A system of sending data over long distances cpmsisting of a transmitter, a transmission channel and a receiver | Water Distribution Grades 1&2
| What is a remote terminal unit (RTU) | A compurter terminal used to monitor the status of control element, monitor and transmit imputs from insrtuments, respond to data requests and demands form the master station. | A compurter terminal used to monitor the status of control element, monitor and transmit imputs from insrtuments, respond to data requests and demands form the master station. | Water Distribution Grades 1&2
| What is a control terminal unit (CTU)? | A receiving device in a digital telemetry system | A receiving device in a digital telemetry system | Water Distribution Grades 1&2
| What does SCADA stand for | Supervisory control and data acquisition | Supervisory control and data acquisition | Water Distribution Grades 1&2
| What does SCADA do? | A Methodology incolcing equipment that both acquires data on an operation and provides limited or total control of equipment to the data. | A Methodology incolcing equipment that both acquires data on an operation and provides limited or total control of equipment to the data. | Water Distribution Grades 1&2
Chapter 13 | MOTORS
| What is the simplest of all AC motors a. Synchronous motor b. Squirrel-cage induction motor c. Wound-rotor induction motor d. Split-phase motor | b | Squirrel-cage induction motor
| Starters are typically used on motors a. larger than fractional horsepower b. of fractional horsepower c. of all horsepower ratings d. when gasoline is unavailable | a | larger than fractional horsepower
| In what type of motor is power applied to the winding in such a way that a revolving magnetic field is established a. Synchronous motor b. Squirrel-cage induction motor c. Wound-rotor induction motor d. Split-phase motor | a | synchronous motor
| Operators should check idle speed, oil pressure, water temperature and all other operating indicators. a. before starting the engine b. exactly one hour after starting the engine c. soon after starting the engine d. on an as-needed basis | c | soon after starting the engine
| What is the maximum ambient temperature at which motors are designed to function. | 104 F (40C) | 104 F (40C)
| What type of motor is used for most large pumps | Three-phase motor | Three-phase motor
| What is the primary use of diesel engines | To power emergency generatores for pump stations and water treatment plants | To power emergency generatores for pump stations and water treatment plants
| How should a system ensure that engines used for emergency services will function whan needed. | Excerise inder load in a predetermined schedule | Excerise inder load in a predetermined schedule
| What device is used when the starting current of a mototr is so high that it may damage the electrical system or deprive other operating motors of sufficient current? | Reduced-voltage controller | Reduced-voltage controller
| What is single phase | Alternating current (AC) power in which the curremt flows reaches a peak in each direction only once per cycle. | Alternating current (AC) power in which the curremt flows reaches a peak in each direction only once per cycle.
| What is Three Phase | Alternating current (AC) power in which the curremt flows reaches three peaks in each direction during each cycle. | Alternating current (AC) power in which the curremt flows reaches three peaks in each direction during each cycle.
| What are the Three main classes of motors used in distribution systems | Squirrel-cage induction, Synchronous and wound-rotor induction | Squirrel-cage induction, Synchronous and wound-rotor induction
| What is the most common type of induction electric motor, and why did it get this name? | Squirrel cage induction motor. The rotor consists of a series of alluminum cor copper bars in parallel to the shaft resembiling a squirrel cage | Squirrel cage induction motor. The rotor consists of a series of alluminum cor copper bars in parallel to the shaft resembiling a squirrel cage
Chapter 14
| The "heart" of a pump is called the a. Volute case b. Impeller c. Motor d. pump | b | The impeller
| Which device serves the same function as the packing? a. Inline suction glad b. Packing gland c. Mechanical seal d. Lantern seal | c | Mechanical seal
| Which of the following is used to stop air leakage into the casing around a pump shaft? a. Packing Gland b. Lantern ring c. Seals d. Shaft Seals | c | seals
| Which of the following is at the top of a stuffing box? a. Packing Gland b. Lantern ring c. Mechanical Seal d. Seal cage | a | Packing gland
| Which assembly holds the lantern ring and packing? a. Shaft assembly b. Casing ring assembly c. Packing gland casing d. Stuffing Box | d | Stuffing Box
| Which type of valve is used to isolate a pump on the suction side? a. Butterfly valve b. Globe valve c. Gate valve d. Ball valve | c | Gate valve
| Packing is designed to a. Add lubricant to the shaft b. Expand and deteriorate with normal use c. Protect the shaft d. Wear and deteriorate with normal use | d | wear and deteriorate with normal use.
| Why is it so important to monitor the speed of a variable-speed pump? a. To prevent excessive temperatures from developing b. To prevent vibrations c. To prevent speed oscillation from occurring d. To prevent cavitation from occurring | d | To prevent cavitation from occurring
| What type of pump has an impeller rotating in a channel of constant cross-sectional area, which imparts mixed or radial flow to the water? | Vertical turbine pump | Vertical turbine pump
| What type of pump uses closely meshed gears, vanes, or lobes rotating within a close-fitting chamber? | Rotary pumps | Rotary pumps
| To prevent excessive circulation of water between the impeller discharge and suction areas, what components are used to create a flow restriction? | Wear rings | Wear rings
| To prevent leakage at the point where the shaft protrudes through the case, what components may be used to seal the space between the shaft and the case? | Either packing rings or mechanical seals | Either packing rings or mechanical seals
| What is a velocity pump | It’s a type of pump with a fast-spinning part that makes the fluid move faster. Then, the pump turns that fast-moving fluid into higher pressure. | A general class of pump that uses a rapidily turning impeller to increase Velocity of a fluid. The pump casing can then convert that high velocity fluid into low velocity, high pressure head. It’s a type of pump with a fast-spinning part that makes the fluid move faster. Then, the pump turns that fast-moving fluid into higher pressure.
| What is an impeller | The rotating set of vanes that forces water through a pump | The rotating set of vanes that forces water through a pump
| What are two main designs of velocity pumps? | Centifugal and Turbine | Centifugal and Turbine
| What is the key difference between Centrifugal and turbine pumps? | Centrifugal has a spinning impeller that throws water outwart and a case that decreases velocity to increase pressure, while a Turbine uses stationary Guide vanes. A centrifugal pump has a spinning part that throws water outward, and its case slows the water down to raise pressure. A turbine pump, on the other hand, uses fixed guide vanes to control the flow. | Centrifugal has a spinning impeller that throws water outwart and a case that decreases velocity to increase pressure, while a Turbine uses stationary Guide vanes. A centrifugal pump has a spinning part that throws water outward, and its case slows the water down to raise pressure. A turbine pump, on the other hand, uses fixed guide vanes to control the flow.
| What is slip in the context of a pump | The percentage of water taken into the suction ensd that is not discharged due to clearances. | The percentage of water taken into the suction ensd that is not discharged due to clearances.
| Describe aspects of a vertical turbine pump | A centrifugal pump, commonly of the multistage diffuser type that shaft is vertically mounted. | A centrifugal pump, commonly of the multistage diffuser type that shaft is vertically mounted.
| What are three common types of vertical pumps. | Deep-well a long drive shaft with submerged lower shaft multi stage impeller and diffuser 2. Submersible pump- Multi staged centrifugal or turbine pump where the entire pump and motor is below the water level 3. Booster Pump- turbine pump with motor and pump mounted close togeather and installed in a sump. Deep-well pump: It has a long shaft with the lower part underwater, using multiple impellers and diffusers. Submersible pump: A multi-stage pump where both the motor and pump are fully underwater. Booster pump: A turbine pump with the motor and pump placed close together, usually installed in a pit or sump. | 1. Deep-well a long drive shaft with submerged lower shaft multi stage impeller and diffuser 2. Submersible pump- Multi staged centrifugal or turbine pump where the entire pump and motor is below the water level 3. Booster Pump- turbine pump with motor and pump mounted close togeather and installed in a sump. Deep-well pump: It has a long shaft with the lower part underwater, using multiple impellers and diffusers. Submersible pump: A multi-stage pump where both the motor and pump are fully underwater. Booster pump: A turbine pump with the motor and pump placed close together, usually installed in a pit or sump. |  |  |  | Deep-well a long drive shaft with submerged lower shaft multi stage impeller and diffuser 2. Submersible pump- Multi staged centrifugal or turbine pump where the entire pump and motor is below the water level 3. Booster Pump- turbine pump with motor and pump mounted close togeather and installed in a sump. Deep-well pump: It has a long shaft with the lower part underwater, using multiple impellers and diffusers. Submersible pump: A multi-stage pump where both the motor and pump are fully underwater. Booster pump: A turbine pump with the motor and pump placed close together, usually installed in a pit or sump.
| What is a rotary pump | A type of a positive displacement pump consisting of elements resembling gears that rotate in a close- fitting pump case. | A type of a positive displacement pump consisting of elements resembling gears that rotate in a close- fitting pump case.
| What is a foot valve? | A check valve placed in the bottom of the suction pipe in a pump, which opens to allow water to enter the suction pipe but closes to prevent water from passing out of it at the bottom | A check valve placed in the bottom of the suction pipe in a pump, which opens to allow water to enter the suction pipe but closes to prevent water from passing out of it at the bottom
| What can happen if a pump runs to fast? | Cavitation | Cavitation |  |  |  | Cavitation is a condition that can occur when pumps are run too fast or water is forced to changed direction quickly and a partional vacuum forms.
| What is a wear ring | A brass or bronze ring placed on the impeller and/or casing of a centrifugal pump to control the amount of water that is allowed to leak from the discharge to the suction side of the pump. | A brass or bronze ring placed on the impeller and/or casing of a centrifugal pump to control the amount of water that is allowed to leak from the discharge to the suction side of the pump. |  |  |  | A flow restriction must exist between the impeller discharge and suction areas to prevent excessive circulation of water between the two.
| What are packings? | Rings of graphite-impregnated cotton, flax, or a sythetic materials, used to control leakage along a valve stem or a pump shaft. | Rings of graphite-impregnated cotton, flax, or a sythetic materials, used to control leakage along a valve stem or a pump shaft.
| What is a lantern ring? | A perforated ring placed around the pump shagt in the stuffing box. Water from the pump discharges in piped to the lantern ring so that it will form a liquid seal around the shaft and lubricate the packing | A perforated ring placed around the pump shagt in the stuffing box. Water from the pump discharges in piped to the lantern ring so that it will form a liquid seal around the shaft and lubricate the packing |  |  |  | When a pump operates under suction lift, the impeller inlet is actually operating in a vacume, if it is not sealed a vacume will form. The latern ring prevents this problem.
| Mechanical seal is what? | A seal placed on the pump shaft to prevent water from leaking from the pump along the shaft and air from entering the pump. | A seal placed on the pump shaft to prevent water from leaking from the pump along the shaft and air from entering the pump.
| What is a coupling | A device that connects the pump to the motor shaft. | A device that connects the pump to the motor shaft.
Chapter 15
| What type of meter is most common for individual service lines? | Positive displacement meter | Positive displacement meter
| What are the advantages of a venturi meter | Low friction loss, accurate, low maintenance | Low friction loss, accurate, low maintenance
| When are magnetic meters use | when flow is dirty or corrosice | when flow is dirty or corrosice
| How many meters can be tested on most test benches | Multiple meters can be tested simultaneously | Multiple meters can be tested simultaneously
| Which of the following is not a meter type commonly used on water systems? a. Proportional b. Current c. Magnetic d. Inverse | d | inverse
| Positive-displacement meters_____when they are excessively worn. a. Do not register b. Under register c. Over register d. Register intermittently | b | under register
| When using turbine meters, clogging of the wheel's blades can be prevented by installing a(n) __________ ahead of the meter. a. Venturi device b. Impeller c. Strainer d. restrictor | c | strainer
| What type of meter is used for services where daily use is relatively low, but very high flow rates may be required in an emergency? a. Magnetic meter b. Detector-check meter c. Venturi meter d. Compound meter | b | Detector-check meter
| What type of meter is used for customers that have wide variations in water use a. Magnetic meter b. Detector-check meter c. Venturi meter d. Compound meter | d | Compound meter
| What is a water meter? | A device installed in a pipe undedr pressure for measuring and registering the quantity of water passing through | A device installed in a pipe undedr pressure for measuring and registering the quantity of water passing through
| What is the most common type of meter used through customers service, and how does it work | Positive displacement meter. A chamber of known size measured water volume flowwing through it with a disk or piston. | Positive displacement meter. A chamber of known size measured water volume flowwing through it with a disk or piston.
| What is a compound meter? | A meter consisting of two single meters of different capacities and regulating valve that can read 1 or both meters depending on demand. | A meter consisting of two single meters of different capacities and regulating valve that can read 1 or both meters depending on demand.
| How does a current meter work? | Measures the velocity of moving water. | Measures the velocity of moving water.
| A detector-check meter is used for low daily use application, but may require high flow rates in an emergency (Fire sprinkler system), how does it work? | Low volume uses a nutating disk, High volumes opens a check valve baypassing the nutating disk, high volume water passes through to a positive displacement meter. | Low volume uses a nutating disk, High volumes opens a check valve baypassing the nutating disk, high volume water passes through to a positive displacement meter.
| Current meters are also called what________. | Velocity meters | Velocity meters
| What are three types of Current meters and what do the all have in common? | Turbine, multijet, and Propeller, They all have a turbine or propeller that spins. | Turbine, multijet, and Propeller, They all have a turbine or propeller that spins.
| What is a Proportional? | A meter that diverts a a portion of the main flow through a restriction to a turbine or displacement meter. | A meter that diverts a a portion of the main flow through a restriction to a turbine or displacement meter.
| How does a venturi meter measure flow? | By a comparision of the pressure at the throat and a point upstream of the throat in a venturi tube. | By a comparision of the pressure at the throat and a point upstream of the throat in a venturi tube.
| What is the principle of a orifice meter? | The entire flow passes through a orifice creating a pressure drop proportional to the flow. | The entire flow passes through a orifice creating a pressure drop proportional to the flow.
| How does a magnetic meter measure flow? | The movement of water induces an electrical current proportional to the rate of flow. | The movement of water induces an electrical current proportional to the rate of flow.
| What type of meter uses sound generating and receiving sensors (transducers) attached to a side of a pipe? | An ultrasonic meter. | An ultrasonic meter.
Chapter 16
| One of chlorine's advantages is that it a. is not influenced much by pH changes b. does not produce chlorinated by-products c. has a persistent residual d. does not cause taste and odor problems | c | has a persistent residual
| Chlorine gas is____________ times heavier than air a. 1.5 b. 2.5 c. 3.5 d. 4.5 | b | 2.5
| After a water storage tank has been chlorinated, which bacteriological test must prove negative before the tank is put back into service? a. Gram-negative test b. HPC test c. Coliforms test d. Chloramine test | c | Coliform test
| Sodium hypochlorite (NaOCl) solution is available with______ available chlorine? a. 2-5% b. 5-20% c. 25-50% d. 50-70% | b | 5-20%
| Booster Chlorination is chlorine added a. In the coagulation mixing chamber b. Before the filters c. At the Clearwell d. Somewhere in the distribution system | d | somewhere in the distribution system
| Chlorine cylinders hold________ of chlorine a. 100 lb b. 150 lb c. 200 lb d. 350 lb | b | 150lb (68kg)
| Why would a system need a booster chlorination station? | To maintain a more consistent chlorine residual throughout the system | To maintain a more consistent chlorine residual throughout the system
| In the C x T equation, that does the C represent? | A known concentration of disinfectant | A known concentration of disinfectant
| What is the term for the total of all the compounds with disinfecting properties, plus any remaning uncombined chlorine? | Chlorine residual | Chlorine residual
| What is the term for a venturi device that pulls chlorine gas into a passing stream of dilution water, forming a strong solution of chlorine and water? | Injector | Injector
| What is the term for a chlorination method increasingly used water treatment plants because of its relative safety ( as a compound gaseous chlorine) and its ease of use? | Hypochlorination | Hypochlorination
| What is the definition of disinfection | The water treatment process that kills disease causing organisms in water, usually by the addition of chlorine | The water treatment process that kills disease causing organisms in water, usually by the addition of chlorine
| What is C x T | The product of the residual disinfectant concentration C in mg/L and the corresponding disinfectant contact time T in minutes. | The product of the residual disinfectant concentration C in mg/L and the corresponding disinfectant contact time T in minutes.
| Define chlorine demand | The amount of chlorine that will combiine with organic and inorganic materials to form chlorine compounds | The amount of chlorine that will combiine with organic and inorganic materials to form chlorine compounds
| Define Chlorine residual | The totalof all the compounds with disinfecting properties, plus any remaining uncombined chlorine. | The totalof all the compounds with disinfecting properties, plus any remaining uncombined chlorine.
| What is chlorine Dosage equation | Chlorine Demand+Total Chlorine Residual | Chlorine Demand+Total Chlorine Residual
| What is the chlorine residual equation? | Combined Chlorine +Free Chlorine | Combined Chlorine +Free Chlorine
| What is the reaction between chlorine (Cl2) and Water (HOH) | CL2 + HOH = HOCL (hypochlorous acid) +HCL (hydrochloric acid) | CL2 + HOH = HOCL (hypochlorous acid) +HCL (hydrochloric acid)
| Regardless of type of chlorine added, what is desired chemical after the CL2 has reacted with water? | Hypochlorous acid (HOCL) | Hypochlorous acid (HOCL)
| Depending on the pH of the water, what two acids can form water reacting with chlorine? | Hypochlorous acid (HOCL) or OCL- (hypochlorite ion) | Hypochlorous acid (HOCL) or OCL- (hypochlorite ion)
| What is the chemical reaction of Calcium Hypochlorite Ca(OCL)2 and water 2(HOH) | hypochlorous acid (2HOCL) + Ca(OH)2 | hypochlorous acid (2HOCL) + Ca(OH)2
| What is the chemical reaction of sodium Hypochlorite Na(OCL) and water (HOH) | Hypochlorous acid (HOCL) + Sodium hydroxide (NaOH) | Hypochlorous acid (HOCL) + Sodium hydroxide (NaOH)
| What are the 3 most common forms of chlorine added and their associated strengths (in order from strogest to weakest of chlorine availabilty)? | Chlorine gas at 100%, Calcium Hypochlorite at 65% and sodium Hypochlorite at 5-15% | Chlorine gas at 100%, Calcium Hypochlorite at 65% and sodium Hypochlorite at 5-15%
| What is breakpoint chlorination? | The point at which the chlorine dosage has satisfied the chlorine demand. | The point at which the chlorine dosage has satisfied the chlorine demand.
| How much chlorine gas does a chlorine cylinder hold? | A chlorine cylinder holds 150 pounds of chlorine and a total filled weight of 250-285 lb | A chlorine cylinder holds 150 pounds of chlorine and a total filled weight of 250-285 lb
| How much chlorine gas does a ton container hold? | A ton container 2000Lb of chlorine and weighs about 3700 lb when full. | A ton container 2000Lb of chlorine and weighs about 3700 lb when full.
| Why do chlorine Ton Containers have two valves? | Designed to rest on their side, Two valves are are equpped to draw gas or liquid. | Designed to rest on their side, Two valves are are equpped to draw gas or liquid.
| What are the 4 componets of Gas chlorine feeding system? | Weighted scales, Valves and piping, Chlorinator and an injector or diffuser. | Weighted scales, Valves and piping, Chlorinator and an injector or diffuser.
| What is a chlorinator? | Any device that is used to add chlorine to water. | Any device that is used to add chlorine to water.
| What is the function of an injector? | The portion of a chlorination system that feeds the chlorine solution into a pipe inder pressure. | The portion of a chlorination system that feeds the chlorine solution into a pipe inder pressure.
| What is the function of the diffuser in a chlorine feed system? | A section of a perforated pipe or porous plates used to inject a gas, a type of pump. A perferated pipe used to uniformaly disperses the chlorine CL2 solution. | A section of a perforated pipe or porous plates used to inject a gas, a type of pump. A perferated pipe used to uniformaly disperses the chlorine CL2 solution.
| What is the role of a booster pump? | To provide the water pressure necessary to make the injector operate properly. | To provide the water pressure necessary to make the injector operate properly.
| What is the function of a chlorine evaporator? | A heating device used to convert liquid chlorine to chlorine gas. | A heating device used to convert liquid chlorine to chlorine gas.
| Define Hypochlorination | Chlorination using solutions of calcium or sodium hypochlorite | Chlorination using solutions of calcium or sodium hypochlorite
| What factors can affect C x T values? | Temperature,pH, and concentration | Temperature,pH, and concentration
| What does DBPs stand for? | Disinfection By-products. | Disinfection By-products.
| What are the two common DBPs | trihalomethanes (TTHMs) and Haloacetic acids (HAA's) | trihalomethanes (TTHMs) and Haloacetic acids (HAA's)
| How are DBPs formed? | These by-products are formed when chlorine is added to water that contains the necessary types and amounts of natural organic matter (NOM) | These by-products are formed when chlorine is added to water that contains the necessary types and amounts of natural organic matter (NOM)
Chapter 17
| Precipitative softening water treatment plants try to end up with distribution system water that is a. Slightly scale forming b. Moderately scale forming c. neutral d. In equilibrium | a | Slightly scale forming
| There are two major objectives for drinking water distribution system operational policies: 1. maintain water quality from the point of entry into the distribution system to the point of use and 2. ? a. Keep operating expenses under budget b. Make sure customers do not waste water c. Educate customers about water safety d. Maintain adequate pressure and deliver adequate flow | d | maintain adequate pressure and deliver adequate flow
| The goal of a well-managed distribution systems should be to provide water to customers taps that has _______ from the point of entry into the system. a. Not changed b. Gained valuable nutrients c. Decrease dramatically in pH d. Become better tasting | a | not changed
| What factor generally determines the need for larger mains? a. Fire flow requirements b. pH concerns c. Potability issues d. Number of customers served | a | Fire flow requirments
| Which of the following is not a major factor in storage facility design? a. Preventing dead zones b. Selecting and maintaining the correct materials of constructions c. Staying under budget to allow for design modification d. Providing adequate and appropriate cathodic protection to prevent or control corrosion | c | Staying under budget to allow for design modifications
| Where do many distribution systems water quality problems develop? | Finished water storage facilities | Finished water storage facilities
| What is a hydraulic system model? | A computer simulation of the behavior of physical facilities and water within the distribution system | A computer simulation of the behavior of physical facilities and water within the distribution system
| What may occur at pressure zone boundaries? | May form dead end boundaries | May form dead end boundaries
| What should be considerd when designing storage facilities? | Inspection, maintenance, monitoring and mixing practices | Inspection, maintenance, monitoring and mixing practices
| In assessing water quality, what rule is of particular intrest to distribution system system operaors? | Lead and Copper Rule | Lead and Copper Rule |  |  |  | The purpose of a routine sampling plan is to examine characteristics of water quality in the distribution system as the water moves from source to tap. The plan must include all samples to meet regulatory requirments. Of particular interest to distribution system operators is the US Environmental Protection agency Lead and Copper Rule. This regulation requires special testing of samples collected from residences and in the distribution system.
Chapter 18
| Samples to be tested for coliforms are collected in plastic bottles that must contain? | Sodium thiosulfate | Sodium thiosulfate
| The volume of a sample for coliform compliance is? | 100mL | 100mL
| If a water sample is not analyzed immediately for chlorine residual, it is accepatble if it is analyzed within? | 15 minutes | 15 minutes
| The best choice to collect a water sample from a customer's faucet when responding to a complaint would be? | faucet without threads | faucet without threads
| When measuring for free chlorine residual, which method is the quickest and simplest? | DPD colorimetric methods | DPD colorimetric methods
| A_______ is a single-volume sample collected at one time from one place? | grab samples | grab samples
| Under the Ground water rule (GWR), what type of sampling is required for larger systems for chlorine residual? | continuous | continuous
| What are three broadly classified areas from which samples are generally collected? | Raw-water supply, treatment plant and distribution system | Raw-water supply, treatment plant and distribution system
| Consistency among laboratories in analytical results is overseen by state primacy programs and by what organization? | USEPA | USEPA
| If samples arrive at a laboratory past the specified holding time following collection, the laboratory must do what? | Reject the sample | Reject the sample
| A grab sample is what? | A single sample collected at one time from a single point? | A single sample collected at one time from a single point?
| What is a composite sample? | A series of individual or grab samples taken at different times from the same sampling point and mixed togeather. Not for bacteriological examination. | A series of individual or grab samples taken at different times from the same sampling point and mixed togeather. Not for bacteriological examination.
| Representative sample is what? | A collected sample that accurately reflects the composition of water to be tested | A collected sample that accurately reflects the composition of water to be tested
| What are four general classes of chemical contaminants that are monitoried? | Inorganics (IOCs), Synthetic Organics (SOCs), Volatile Organics (VOCs) and Radionuclides | Inorganics (IOCs), Synthetic Organics (SOCs), Volatile Organics (VOCs) and Radionuclides
| What is a chain of custody for a water sample? | A written record of the sample's history from the time of collection to the time of analysis and subsequent disposal. | A written record of the sample's history from the time of collection to the time of analysis and subsequent disposal.
Chapter 19
| What is the likelihood of a swimming pool creating a cross-connection that could contaminate a potable water supply? | Moderately likely | Moderately likely
| What is the likelihood of a sewage pump creating a cross-connection that could contaminate a potable water supply | Highly likely | Highly likely
| What type of backflow preventer consist of two spring-loaded check valves with a pressure-regulated relief valve located between them? | Reduced pressure zone backflow preventer | Reduced pressure zone backflow preventer
| What is a utility's first line of defense against potential legal liability in case a public health problems resulting from a cross-connection? | Maintain complete records | Maintain complete records
| What is the best method to prevent backflow? | Air Gap | Air Gap
| How frequently do most regulations require testing of backflow-prevention devices? | Anunually | Anunually
| What is a cross-connection? | Any connection between the potable water supply and a source of contamination | Any connection between the potable water supply and a source of contamination
| Give two examples of cross-connections | cooling towers, boilers, service sinks | cooling towers, boilers, service sinks
| Give some examples of causes of backflow? | Pressurized chemical storages, high-pressure boilers | Pressurized chemical storages, high-pressure boilers
| What is the term for a cross-connection for which something must be done to complete the connection | potential cross-connection. | potential cross-connection.
| Define backflow | A hydraulic condition caused by a difference in pressures, in which nonpotable water or other fluids flow into a potable water systems | A hydraulic condition caused by a difference in pressures, in which nonpotable water or other fluids flow into a potable water systems
| Define backpresssure | A condition in which a pump, boiler, or other equipment produces a pressure greater than the water supply pressure. | A condition in which a pump, boiler, or other equipment produces a pressure greater than the water supply pressure.
| What is a Backsiphonage? | A condition in which the pressure in the distribution system is less than atmospheric pressure, which allows contamination to enter a water system through a cross-connection. | A condition in which the pressure in the distribution system is less than atmospheric pressure, which allows contamination to enter a water system through a cross-connection.
| What is a Cross- Connection | Any arrangement of pipes, fitting, fixtures, or devices that connects a nonpotable systems to a potable water systems. | Any arrangement of pipes, fitting, fixtures, or devices that connects a nonpotable systems to a potable water systems.
| What is the difference between an actual Cross-connection and a potentail cross-connection | Actual directly connects non-potable water to potable at all times vs. indirectly connecting that may or may not be present all the time | Actual directly connects non-potable water to potable at all times vs. indirectly connecting that may or may not be present all the time
| What is an Air Gap | in Plumbing, the unobstructed vertical distance through the free atmosphere between the lowest opening from any pipe or outlet and sump | in Plumbing, the unobstructed vertical distance through the free atmosphere between the lowest opening from any pipe or outlet and sump
| A Reduced Pressure Zone (RPZ) backflow preventer is what? | A mechanical device consisting of two independently operating, spring loaded check valves with a reduced-pressure zone between the check valves | A mechanical device consisting of two independently operating, spring loaded check valves with a reduced-pressure zone between the check valves
| How does a double check valve backlow preventer differ from a RPZ | A double check valve does not have a relief valve. | A double check valve does not have a relief valve.
| How does a Vacuum breaker work? | A mechanical device that allows air into the piping system thereby preventing backflow that could cause a partial vacuum. | A mechanical device that allows air into the piping system thereby preventing backflow that could cause a partial vacuum.
Chapter 20
| Which type of maps should not overlap each other? | A Sectional Map | A Sectional Map
| Comprehensive maps of medium to large systems generally have scales ranging from | 500-1000 feet to an inch | 500-1000 feet to an inch
| Sectional maps generally have scales ranging from | 50-100 feet to an inch | 50-100 feet to an inch
| A comprehensive map should be | As large as possible | As large as possible
| On a plan and profile drawing, what does the abbreviation EL mean? | Elevation | Elevation
| What type of map is also referred to as a wall map | Comprehensive map | Comprehensive map
| What type of map, commonly called a plat, is a series of maps covering sections of the water system | Sectional map | Sectional map
| What is the term for a computerized program used to manage data relating to geographic locations within a water distribution system? | Automated mapping/facility management/geographic information system | Automated mapping/facility management/geographic information system
| What does a comprehensive map contain? | A map that provides a clear picture on the entire distribution system. It usually indicates the locations of mains, hydrants,valves,tanks pumps and pressure zones. | A map that provides a clear picture on the entire distribution system. It usually indicates the locations of mains, hydrants,valves,tanks pumps and pressure zones.
| What is a suctional map. | A detailed map of a section of the distrubution system with exact locations of system component | A detailed map of a section of the distrubution system with exact locations of system component
| What is a plat | A map showing street names, locations and identifications of mains, valves and hydrants. | A map showing street names, locations and identifications of mains, valves and hydrants.
| What is on a plan and profile drawings | Engineering drawings showing depth of pipe, locations and distances from reference points. | Engineering drawings showing depth of pipe, locations and distances from reference points.
Chapter 21
| Who is responsible for maintaining safe working conditions | All water utilitiy personnel | All water utilitiy personnel
| What item should be worn whenever a worker is in a trench or has somone working above them or near electrical equipment. | A hardhat | A hardhat
| When lifting a load that is too heavy or too large to lift comfortably, | use a mechanical device to assist in lifting heavy objects | use a mechanical device to assist in lifting heavy objects
| Which of the following in not an example of an accidental disaster that might disrupt water utilities? | Earthquake | Earthquake
| What is the most common injury of distribution system workers? | Back injury | Back injury
| Would a meter pit be a permit-required confined space? | Yes, it may contain hazardous atmophere | Yes, it may contain hazardous atmophere
| Under what conditions is cave-in protection always required? | All excavations atleast 5 ft (1.5 M) in depth | All excavations atleast 5 ft (1.5 M) in depth
| What three chemicals are commonly used to disinfect mains and others facilities? | Liquid chlorine sodium and calcium hypochlorite | Liquid chlorine sodium and calcium hypochlorite
Chapter 22
| What are the basic elements to good customer relations? | Good communications, caring and courtesy | Good communications, caring and courtesy
| What should meter readers do when asked a question to which they don't know the answer? | Tell the customer that they don’t know but will find out and get back to them. | Tell the customer that they don’t know but will find out and get back to them.
| What should customers be told when water service must be temporarily stopped? | Notify them with enough time so they can prepare. | Notify them with enough time so they can prepare.
| ________ generally presents the greatest exposure to the public and can have the greatest impact in ensuring public confidence. | Water distribution personal, employees, operators, workers, | Water distribution personal, employees, operators, workers,
| ________ should be viewed as an opportunity to improve communications and build goodwill | Every customer contact | Every customer contact
| If damage to a customer's property occures, | Property must be restored to its original state before workers leave the site | Property must be restored to its original state before workers leave the site
| Shutoffs should be scheduled | to coincide with low-water-use hours | to coincide with low-water-use hours
| What is the general rule for talking to reporters? | Don't do it. | Don't do it.
| What is public relations | The methods and activities employed to promote favorable relationships with the public | The methods and activities employed to promote favorable relationships with the public